## License Agreement
SunSpec Alliance
SunSpec Infomation Model Reference
Date Generated: 2016-07-13
This document is generated programatically from the canonical model definitions contained in the SunSpec model repository.
For the most up-to-date version of this document, go to: www.sunspec.org/download
Copyright SunSpec Alliance 2009-2015. All Rights Reserved.
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE AN
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy.
Prepared by the SunSpec Alliance
4030 Moorpark Avenue, Suite 109
San Jose, CA 95117
Website: www.sunspec.org
Email: info@sunspec.org

## Summary
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | Reserved by SunSpec Alliance
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is derived from SunSpec Model Definition XML (SMDX) files, which can be downloaded from www.sunspec.org/modelreference/
Please note that the SMDX files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at http://sunspec.org/download/.
SunSpec Certification
If you would like to have your product SunSpec Certified, please read the information available at http://sunspec.org/sunspec-certified-program/
and then email certification@sunspec.org to schedule your test.

## Index
Model | Label | Description | Notes
1 | Common | All SunSpec compliant devices must include this as the first model
2 | Basic Aggregator | Aggregates a collection of models for a given model id
3 | Secure Dataset Read Request | Request a digial signature over a specifed set of data registers | Used in conjunction witgh Secure Dataset Read Response Model
4 | Secure Dataset Read Response | Compute a digial signature over a specifed set of data registers
5 | Secure Write Request | Include a digial signature along with the control data
6 | Secure Write Sequential Request | Include a digial signature along with the control data
7 | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response | Used in conjunction with a Secure Write Request
8 | Get Device Security Certificate | Security model for PKI
9 | Set Operator Security Certificate | Security model for PKI
10 | Communication Interface Header | To be included first for a complete interface description
11 | Ethernet Link Layer | Include to support a wired ethernet port
12 | IPv4 | Include to support an IPv4 protocol stack on this interface
13 | IPv6 | Include to support an IPv6 protocol stack on this interface
14 | Proxy Server | Include this block to allow for a proxy server
15 | Interface Counters Model | Interface counters
16 | Simple IP Network | Include this model for a simple IPv4 network stack
17 | Serial Interface | Include this model for serial interface configuration support
18 | Cellular Link | Include this model to support a cellular interface link
19 | PPP Link | Include this model to configure a Point-to-Point Protocol link
101 | Inverter (Single Phase) | Include this model for single phase inverter monitoring
102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
103 | Inverter (Three Phase) | Include this model for three phase inverter monitoring
111 | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
112 | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
113 | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
120 | Nameplate | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
121 | Basic Settings | Inverter Controls Basic Settings | Ref 3: 8.4.2.1, Ref 4: 17
122 | Measurements_Status | Inverter Controls Extended Measurements and Status | Ref 3: 8.14.3.2, Ref 4: 17
123 | Immediate Controls | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
124 | Storage | Basic Storage Controls | Ref 3: 8.7.4.2
125 | Pricing | Pricing Signal | Ref 3: 8.7.5.1; Ref 4: 6
126 | Static Volt-VAR | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
127 | Freq-Watt Param | Parameterized Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
128 | Dynamic Reactive Current | Dynamic Reactive Current | Ref 3: 8.10.1.2; Ref 4: 12
129 | LVRTD | LVRT Must Disconnect | Ref 4: 11
130 | HVRTD | HVRT Must Disconnect | Ref 4: 11
131 | Watt-PF | Watt-Power Factor | Ref 3: 8.11.1.2
132 | Volt-Watt | Volt-Watt | Ref 3: 8.12.1.2
133 | Basic Scheduling | Basic Scheduling | Ref 2: 2.2.8
134 | Freq-Watt Crv | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
135 | LFRT | Low Frequency Ride-through | Ref 4: 11
136 | HFRT | High Frequency Ride-through | Ref 4: 11
137 | LVRTC | LVRT must remain connected | Ref 4: 11
138 | HVRTC | HVRT must remain connected | Ref 4: 11
160 | Multiple MPPT Inverter Extension Model
201 | Meter (Single Phase)single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
202 | split single phase (ABN) meter
203 | wye-connect three phase (abcn) meter
204 | delta-connect three phase (abc) meter
211 | single phase (AN or AB) meter |  | Float
212 | split single phase (ABN) meter |  | Float
213 | wye-connect three phase (abcn) meter |  | Float
214 | delta-connect three phase (abc) meter |  | Float
220 | Secure AC Meter Selected Readings | Include this model for secure metering
302 | Irradiance Model | Include to support various irradiance measurements
303 | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
304 | Inclinometer Model | Include to support orienation measurements
305 | GPS | Include to support location measurements
306 | Reference Point Model | Include to support a standard reference point
307 | Base Met | Base Meteorolgical Model | This model supersedes model 301
308 | Mini Met Model | Include to support a few basic measurements
401 | String Combiner (Current) | A basic string combiner | This model is SUPERSEDED by model 403
402 | String Combiner (Advanced) | An advanced string combiner | This model is SUPERSEDED by model 404
403 | String Combiner (Current) | A basic string combiner model | This model supersedes model 401
404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
501 | Solar Module | A solar module model supporing DC-DC converter | Float
502 | Solar Module | A solar module model supporing DC-DC converter | Integer
601 | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers | Trackers may include GPS model 305 for location information
801 | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
802 | Battery Base Model
803 | Lithium-Ion Battery Bank Model
804 | Lithium-Ion String Model
805 | Lithium-Ion Module Model
806 | Flow Battery Model
807 | Flow Battery String Model
808 | Flow Battery Module Model
809 | Flow Battery Stack Model
63001 | SunSpec Test Model 1
63002 | SunSpec Test Model 2
64001 | Veris Status and Configuration
64020 | Mersen GreenString
64101 | Eltek Inverter Extension
64110 | OutBack AXS device
64111 | Basic Charge Controller
64112 | OutBack FM Charge Controller

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | All SunSpec compliant devices must include this as the first model
Header |  | 1 |  | 1 | L |  | 65 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address

## 111
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | SM2-MU Device value | StuderInnotec Parameter | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Single Phase) FLOAT |  |  | 111 | uint16 |  |  | R | M | Include this model for single phase inverter monitoring using float values
Header |  | 1 |  | 1 | L |  |  |  | 60 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  |  |  | float32 | A |  | R | M | AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA | Iac grid | 3116 |  | float32 | A |  | R | M | Phase A Current | Connected Phase
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  |  |  | float32 | A |  | R | O | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  |  |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PPVphAB | Phase Voltage AB |  |  |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 12 | 10 | 2 | PPVphBC | Phase Voltage BC |  |  |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 2 | PPVphCA | Phase Voltage CA |  |  |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 16 | 14 | 2 | PhVphA | Phase Voltage AN | Uac grid | 3113 |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 18 | 16 | 2 | PhVphB | Phase Voltage BN |  |  |  | float32 | V |  | R | O | Phase Voltage BN
Fixed Block |  | 20 | 18 | 2 | PhVphC | Phase Voltage CN |  |  |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 22 | 20 | 2 | W | Watts | Pac grid | 3119 |  | float32 | W |  | R | M | AC Power
Fixed Block |  | 24 | 22 | 2 | Hz | Hz | Fac grid | 3122 |  | float32 | Hz |  | R | M | Line Frequency
Fixed Block |  | 26 | 24 | 2 | VA | VA | Sac grid |  |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 28 | 26 | 2 | VAr | VAr |  |  |  | float32 | var |  | R | O | AC Reactive Power
Fixed Block |  | 30 | 28 | 2 | PF | PF |  |  |  | float32 | Pct |  | R | O | AC Power Factor
Fixed Block |  | 32 | 30 | 2 | WH | WattHours | Eac grid IO | 3081 |  | float32 | Wh |  | R | M | AC Energy
Fixed Block |  | 34 | 32 | 2 | DCA | DC Amps |  |  |  | float32 | A |  | R | O | DC Current
Fixed Block |  | 36 | 34 | 2 | DCV | DC Voltage |  |  |  | float32 | V |  | R | O | DC Voltage
Fixed Block |  | 38 | 36 | 2 | DCW | DC Watts |  |  |  | float32 | W |  | R | O | DC Power
Fixed Block |  | 40 | 38 | 2 | TmpCab | Cabinet Temperature | Tbat | 7033 |  | float32 | C |  | R | M | Cabinet Temperature
Fixed Block |  | 42 | 40 | 2 | TmpSnk | Heat Sink Temperature |  |  |  | float32 | C |  | R | O | Heat Sink Temperature
Fixed Block |  | 44 | 42 | 2 | TmpTrns | Transformer Temperature |  |  |  | float32 | C |  | R | O | Transformer Temperature
Fixed Block |  | 46 | 44 | 2 | TmpOt | Other Temperature |  |  |  | float32 | C |  | R | O | Other Temperature
Fixed Block |  | 48 | 46 | 1 | St | Operating State |  |  |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 49 | 47 | 1 | StVnd | Vendor Operating State |  |  |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 50 | 48 | 2 | Evt1 | Event1 |  |  |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 52 | 50 | 2 | Evt2 | Event Bitfield 2 |  |  |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 54 | 52 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  |  |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 56 | 54 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  |  |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 58 | 56 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  |  |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 60 | 58 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  |  |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  |  | ggOFF |  |  |  | 1
enum16 | St |  |  |  | ggSLEEPING |  |  |  | 2
enum16 | St |  |  |  | ggSTARTING |  |  |  | 3
enum16 | St |  |  |  | ggMPPT | MPPT |  |  | 4 | [5 empty] | Device is auto tracking maximum power point
enum16 | St |  |  |  | ggTHROTTLED |  |  |  | 5
enum16 | St |  |  |  | ggSHUTTING_DOWN |  |  |  | 6
enum16 | St |  |  |  | ggFAULT |  |  |  | 7
enum16 | St |  |  |  | ggSTANDBY |  |  |  | 8
enum16 | St |  |  |  |  | Off |  |  | 8 | [5 empty] | Device is not operating
enum16 | St |  |  |  |  | Sleeping |  |  | 8 | [5 empty] | Device is sleeping / auto-shudown
enum16 | St |  |  |  |  | Starting |  |  | 8 | [5 empty] | Device is staring up
enum16 | St |  |  |  |  | Throttled |  |  | 8 | [5 empty] | Device is operating at reduced power output
enum16 | St |  |  |  |  | Shutting down |  |  | 8 | [5 empty] | Device is shutting down
enum16 | St |  |  |  |  | Fault |  |  | 8 | [5 empty] | One or more faults exist
enum16 | St |  |  |  |  | Standby |  |  | 8 | [5 empty] | Device is in standby mode
bitfield32 | Evt1 |  |  |  | GROUND_FAULT | Ground fault |  |  | 0
bitfield32 | Evt1 |  |  |  | DC_OVER_VOLT | DC over voltage |  |  | 1
bitfield32 | Evt1 |  |  |  | AC_DISCONNECT | AC disconnect open |  |  | 2
bitfield32 | Evt1 |  |  |  | DC_DISCONNECT | DC disconnect open |  |  | 3
bitfield32 | Evt1 |  |  |  | GRID_DISCONNECT | Grid shutdown |  |  | 4
bitfield32 | Evt1 |  |  |  | CABINET_OPEN | Cabinet open |  |  | 5
bitfield32 | Evt1 |  |  |  | MANUAL_SHUTDOWN | Manual shutdown |  |  | 6
bitfield32 | Evt1 |  |  |  | OVER_TEMP | Over temperature |  |  | 7
bitfield32 | Evt1 |  |  |  | OVER_FREQUENCY | Frequency above limit |  |  | 8
bitfield32 | Evt1 |  |  |  | UNDER_FREQUENCY | Frequency under limit |  |  | 9
bitfield32 | Evt1 |  |  |  | AC_OVER_VOLT | AC Voltage above limit |  |  | 10
bitfield32 | Evt1 |  |  |  | AC_UNDER_VOLT | AC Voltage under limit |  |  | 11
bitfield32 | Evt1 |  |  |  | BLOWN_STRING_FUSE | Blown String fuse on input |  |  | 12
bitfield32 | Evt1 |  |  |  | UNDER_TEMP | Under temperature |  |  | 13
bitfield32 | Evt1 |  |  |  | MEMORY_LOSS | Generic Memory or Communication error (internal) |  |  | 14
bitfield32 | Evt1 |  |  |  | HW_TEST_FAILURE | Hardware test failure |  |  | 15

## 160
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | SM2-MU Device value | StuderInnotec Parameter | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Multiple MPPT Inverter Extension Model | 160 | - | 160 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 28 | - | 8 + (RB Count * 20) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DCA_SF | Current Scale Factor | -2 | - |  | sunssf |  |  | R | O
Fixed Block |  | 3 | 1 | 1 | DCV_SF | Voltage Scale Factor | -2 | - |  | sunssf |  |  | R | O
Fixed Block |  | 4 | 2 | 1 | DCW_SF | Power Scale Factor |  |  |  | sunssf |  |  | R | O
Fixed Block |  | 5 | 3 | 1 | DCWH_SF | Energy Scale Factor | -2 | - |  | sunssf |  |  | R | O
Fixed Block |  | 6 | 4 | 2 | Evt | Global Events |  |  |  | bitfield32 |  |  | R | O
Fixed Block |  | 8 | 6 | 1 | N | Number of Modules | 1 | - |  | count |  |  | R | O
Fixed Block |  | 9 | 7 | 1 | TmsPer | Timestamp Period |  |  |  | uint16 |  |  | R | O
Repeating Block |  | 10 | 0 | 1 | ID | Input ID |  |  |  | uint16 |  |  | R | O
Repeating Block |  | 11 | 1 | 8 | IDStr | Input ID String |  |  |  | string |  |  | R | O
Repeating Block |  | 19 | 9 | 1 | DCA | DC Current | Idc bat | 3095 |  | uint16 | A | DCA_SF | R | O
Repeating Block |  | 20 | 10 | 1 | DCV | DC Voltage | Udc bat | 3092 |  | uint16 | V | DCV_SF | R | O
Repeating Block |  | 21 | 11 | 1 | DCW | DC Power |  |  |  | uint16 | W | DCW_SF | R | O
Repeating Block |  | 22 | 12 | 2 | DCWH | Lifetime Energy | Edc inv IO | 3078 |  | acc32 | Wh | DCWH_SF | R | O
Repeating Block |  | 24 | 14 | 2 | Tms | Timestamp |  |  |  | uint32 | Secs |  | R | O
Repeating Block |  | 26 | 16 | 1 | Tmp | Temperature | Tbat | 7033 |  | int16 | C |  | R | O
Repeating Block |  | 27 | 17 | 1 | DCSt | Operating State |  |  |  | enum16 |  |  | R | O
Repeating Block |  | 28 | 18 | 2 | DCEvt | Module Events |  |  |  | bitfield32 |  |  | R | O
bitfield32 | Evt |  |  |  | GROUND_FAULT | Ground Fault |  |  | 0
bitfield32 | Evt |  |  |  | INPUT_OVER_VOLTAGE | Input Over Voltage |  |  | 1
bitfield32 | Evt |  |  |  | RESERVED | Reserved |  |  | 19
bitfield32 | Evt |  |  |  | DC_DISCONNECT | DC Disconnect |  |  | 3
bitfield32 | Evt |  |  |  | CABINET_OPEN | Cabinet Open |  |  | 5
bitfield32 | Evt |  |  |  | MANUAL_SHUTDOWN | Manual Shutdown |  |  | 6
bitfield32 | Evt |  |  |  | OVER_TEMP | Over Temperature |  |  | 7
bitfield32 | Evt |  |  |  | BLOWN_FUSE | Blown Fuse |  |  | 12
bitfield32 | Evt |  |  |  | UNDER_TEMP | Under Temperature |  |  | 13
bitfield32 | Evt |  |  |  | MEMORY_LOSS | Memory Loss |  |  | 14
bitfield32 | Evt |  |  |  | ARC_DETECTION | Arc Detection |  |  | 15
bitfield32 | Evt |  |  |  | TEST_FAILED | Test Failed |  |  | 20
bitfield32 | Evt |  |  |  | INPUT_UNDER_VOLTAGE | Under Voltage |  |  | 21
bitfield32 | Evt |  |  |  | INPUT_OVER_CURRENT | Over Current |  |  | 22
enum16 | DCSt |  |  |  | OFF | Off |  |  | 1
enum16 | DCSt |  |  |  | SLEEPING | Sleeping |  |  | 2
enum16 | DCSt |  |  |  | STARTING | Starting |  |  | 3
enum16 | DCSt |  |  |  | MPPT | MPPT |  |  | 4
enum16 | DCSt |  |  |  | THROTTLED | Throttled |  |  | 5
enum16 | DCSt |  |  |  | SHUTTING_DOWN | Shutting Down |  |  | 6
enum16 | DCSt |  |  |  | FAULT | Fault |  |  | 7
enum16 | DCSt |  |  |  | STANDBY | Standby |  |  | 8
enum16 | DCSt |  |  |  | TEST | Test |  |  | 9
enum16 | DCSt |  |  |  | RESERVED | Reserved |  |  | 19
bitfield32 | DCEvt |  |  |  | GROUND_FAULT | Ground Fault |  |  | 0
bitfield32 | DCEvt |  |  |  | INPUT_OVER_VOLTAGE | Input Over Voltage |  |  | 1
bitfield32 | DCEvt |  |  |  | RESERVED | Reserved |  |  | 19
bitfield32 | DCEvt |  |  |  | DC_DISCONNECT | DC Disconnect |  |  | 3
bitfield32 | DCEvt |  |  |  | CABINET_OPEN | Cabinet Open |  |  | 5
bitfield32 | DCEvt |  |  |  | MANUAL_SHUTDOWN | Manual Shutdown |  |  | 6
bitfield32 | DCEvt |  |  |  | OVER_TEMP | Over Temperature |  |  | 7
bitfield32 | DCEvt |  |  |  | BLOWN_FUSE | Blown Fuse |  |  | 12
bitfield32 | DCEvt |  |  |  | UNDER_TEMP | Under Temperature |  |  | 13
bitfield32 | DCEvt |  |  |  | MEMORY_LOSS | Memory Loss |  |  | 14
bitfield32 | DCEvt |  |  |  | ARC_DETECTION | Arc Detection |  |  | 15
bitfield32 | DCEvt |  |  |  | TEST_FAILED | Test Failed |  |  | 20
bitfield32 | DCEvt |  |  |  | INPUT_UNDER_VOLTAGE | Under Voltage |  |  | 21
bitfield32 | DCEvt |  |  |  | INPUT_OVER_CURRENT | Over Current |  |  | 22

## 64400
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer Parameter Read / Write | 64400 | uint16 |  |  | R | M | Special Model to read and write Studer-Innotec device parameters
Header |  | 1 |  | 1 | L |  | 5 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ParNum | Parameter Number |  | uint16 |  |  | RW | M | Parameter number to be read or written (input)
Fixed Block |  | 3 | 1 | 1 | ParType | Parameter Type |  | enum16 |  |  | RW | M | Type of value, corresponding to the parameter (READ: output, WRITE: input) | This type is used for data transfer between Solar Monitor and Studer, see ParValue for its notes.
Fixed Block |  | 4 | 2 | 2 | ParValue | Parameter Value |  | float32 |  |  | RW | M | Read value (output) or value to be written (input) | This value is always in Float32 format.
Fixed Block |  | 6 | 4 | 1 | ParCmd | Parameter Command |  | bitfield16 |  |  | RW | M | Command to be issued (read or write command is set and then this field is polled until the bit gets cleared)
enum16 | ParType |  |  | Name: Integer; Label: Integer32; Value: 0 |  | 32 bit signed value, big endian | Studer INT32 type.
enum16 | ParType |  |  | Name: Enum; Label: Enum16; Value: 1 |  | 32 bit signed value, only 16 bits used | Studer SHORT_ENUM type.
enum16 | ParType |  |  | Name: Byte; Label: Integer8; Value: 2 |  | 32 bit signed value, only 8 bits used | Studer BOOL type.
enum16 | ParType |  |  | Name: Float; Label: Float32; Value: 3 |  | float in 32 bit IEEE 754 format, big endian | Studer FLOAT type.
bitfield16 | ParCmd |  |  | Name: READ; Label: Read Command; Value: 32 |  | Set this bit to initiate a read operation | Also the ParNum field must be written previously or concurrently. ParType and ParValue is an ouput from this command.
bitfield16 | ParCmd |  |  | Name: WRITE; Label: Write Command; Value: 16 |  | Set this bit to initiate a write operation | All 3 other fields ParNum, ParType and ParValue must be written previously or concurrently.

## 64410
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer Xtender Model | 64410 | uint16 |  |  | R | M | Studer-Innotec Xtender Model
Header |  | 1 |  | 1 | L |  | 98 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | xtModel | XT Model |  | string |  |  | R | O | 3124 – 3125
Fixed Block |  | 18 | 16 | 16 | xtFID | XT FID |  | string |  |  | R | O | 3056 – 3057
Fixed Block |  | 34 | 32 | 16 | xtSwVersion | Software Version |  | string |  |  | R | O | 3030 – 3031
Fixed Block |  | 50 | 48 | 2 | xtIdBatteryVoltage | ID Battery Voltage |  | float32 | V |  | R | O | 3127
Fixed Block |  | 52 | 50 | 2 | xtDefinedPhase | Defined Phase |  | float32 |  |  | R | O | 3089
Fixed Block |  | 54 | 52 | 1 | xtState | State |  | enum16 |  |  | R | O | 3049
Fixed Block |  | 55 | 53 | 2 | xtBatteryVoltage | Battery Voltage |  | float32 | V |  | R | O | 3092
Fixed Block |  | 57 | 55 | 2 | xtBatteryChargeCurrent | Battery Charge Current |  | float32 | A |  | R | O | 3095
Fixed Block |  | 59 | 57 | 1 | xtBatteryCyclePhase | Battery Cycle Current |  | enum16 |  |  | R | O | 3010
Fixed Block |  | 60 | 58 | 2 | xtInVoltage | Input Voltage |  | float32 | V |  | R | O | 3113
Fixed Block |  | 62 | 60 | 2 | xtInVoltageMin | Input Voltage Min |  | float32 | V |  | R | O | 3111
Fixed Block |  | 64 | 62 | 2 | xtInVoltageMax | Input Voltage Max |  | float32 | V |  | R | O | 3112
Fixed Block |  | 66 | 64 | 2 | xtInCurrent | Input Current |  | float32 | A |  | R | O | 3116
Fixed Block |  | 68 | 66 | 2 | xtInCurrentMin | Input Current Min |  | float32 | A |  | R | O | 3114
Fixed Block |  | 70 | 68 | 2 | xtInCurrentMax | Input Current Max |  | float32 | A |  | R | O | 3115
Fixed Block |  | 72 | 70 | 2 | xtInFrequency | Input Frequency |  | float32 | Hz |  | R | O | 3122
Fixed Block |  | 74 | 72 | 2 | xtInFrequencyMin | Input Frequency Min |  | float32 | Hz |  | R | O | 3120
Fixed Block |  | 76 | 74 | 2 | xtInFrequencyMax | Input Frequency Max |  | float32 | Hz |  | R | O | 3121
Fixed Block |  | 78 | 76 | 2 | xtInApparentPower | Input Apparent Power |  | float32 | kVA |  | R | O | 3138
Fixed Block |  | 80 | 78 | 2 | xtInActivePower | Input Active Power |  | float32 | kW |  | R | O | 3119
Fixed Block |  | 82 | 80 | 2 | xtOutVoltage | Output Voltage |  | float32 | V |  | R | O | 3021
Fixed Block |  | 84 | 82 | 2 | xtOutCurrent | Output Current |  | float32 | A |  | R | O | 3022
Fixed Block |  | 86 | 84 | 2 | xtOutFrequency | Output Frequency |  | float32 | Hz |  | R | O | 3110
Fixed Block |  | 88 | 86 | 2 | xtOutApparentPower | Output Apparent Power |  | float32 | kVA |  | R | O | 3139
Fixed Block |  | 90 | 88 | 2 | xtOutActivePower | Output Active Power |  | float32 | kW |  | R | O | 3101
Fixed Block |  | 92 | 90 | 1 | xtOperatingState | Operating State |  | enum16 |  |  | R | O
Fixed Block |  | 93 | 91 | 1 | xtTransferRelay | State of Transfer Relay |  | enum16 |  |  | R | O | 3020
Fixed Block |  | 94 | 92 | 1 | xtRemoteEntryState | Remote Entry State |  | enum16 |  |  | R | O | 3086
Fixed Block |  | 95 | 93 | 1 | xtBatteryPriorityActive | Battery Priority Active |  | uint16 |  |  | R | O | 3161
Fixed Block |  | 96 | 94 | 1 | xtAUX1RelayState | State of Auxillary Relay 1 |  | enum16 |  |  | R | O | 3031
Fixed Block |  | 97 | 95 | 1 | xtAUX1RelayMode | Relay AUX 1 Mode |  | enum16 |  |  | R | O | 3054
Fixed Block |  | 98 | 96 | 1 | xtAUX2RelayState | State of Auxillary Relay 2 |  | enum16 |  |  | R | O | 3032
Fixed Block |  | 99 | 97 | 1 | xtAUX2RelayMode | Relay AUX 2 Mode |  | enum16 |  |  | R | O | 3055
enum16 | xtState |  |  | Name: off; Label: Offline; Value: 0
enum16 | xtState |  |  | Name: on; Label: Online; Value: 1
enum16 | xtBatteryCyclePhase |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | xtBatteryCyclePhase |  |  | Name: bulk; Label: Bulk; Value: 1
enum16 | xtBatteryCyclePhase |  |  | Name: absorption; Label: Absorption; Value: 2
enum16 | xtBatteryCyclePhase |  |  | Name: equalise; Label: Equalise; Value: 3
enum16 | xtBatteryCyclePhase |  |  | Name: floating; Label: Floating; Value: 4
enum16 | xtBatteryCyclePhase |  |  | Name: rFloating; Label: R Floating; Value: 5
enum16 | xtBatteryCyclePhase |  |  | Name: perAbsorption; Label: Per Absorption; Value: 6
enum16 | xtBatteryCyclePhase |  |  | Name: mixing; Label: Mixing; Value: 7
enum16 | xtBatteryCyclePhase |  |  | Name: forming; Label: Forming; Value: 8
enum16 | xtOperatingState |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | xtOperatingState |  |  | Name: inverter; Label: Inverter; Value: 1
enum16 | xtOperatingState |  |  | Name: charger; Label: Charger; Value: 2
enum16 | xtOperatingState |  |  | Name: boost; Label: Boost; Value: 3
enum16 | xtOperatingState |  |  | Name: injection; Label: Injection; Value: 4
enum16 | xtTransferRelay |  |  | Name: opened; Label: Opened; Value: 0
enum16 | xtTransferRelay |  |  | Name: closed; Label: Closed; Value: 1
enum16 | xtRemoteEntryState |  |  | Name: rmEn0; Label: Remote Entry 0; Value: 0
enum16 | xtRemoteEntryState |  |  | Name: rmEn1; Label: Remote Entry 1; Value: 1
enum16 | xtAUX1RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | xtAUX1RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | xtAUX1RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | xtAUX1RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | xtAUX1RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | xtAUX1RelayMode |  |  | Name: manualOn; Label: Manual On; Value: 3
enum16 | xtAUX1RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | xtAUX1RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5
enum16 | xtAUX2RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | xtAUX2RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | xtAUX2RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | xtAUX2RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | xtAUX2RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | xtAUX2RelayMode |  |  | Name: manualOn; Label: Manual On; Value: 3
enum16 | xtAUX2RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | xtAUX2RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5