## License Agreement
SunSpec Alliance
SunSpec Infomation Model Reference
Date Generated: 2016-07-13
This document is generated programatically from the canonical model definitions contained in the SunSpec model repository.
For the most up-to-date version of this document, go to: www.sunspec.org/download
Copyright SunSpec Alliance 2009-2015. All Rights Reserved.
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy. The complete policy of the SunSpec Alliance can be found at www.sunspec.org.
Prepared by the SunSpec Alliance
4030 Moorpark Avenue, Suite 109
San Jose, CA 95117
Website: www.sunspec.org
Email: info@sunspec.org

## Summary
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | Reserved by SunSpec Alliance
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is derived from SunSpec Model Definition XML (SMDX) files, which can be downloaded from www.sunspec.org/modelreference/
Please note that the SMDX files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at http://sunspec.org/download/.
SunSpec Certification
If you would like to have your product SunSpec Certified, please read the information available at http://sunspec.org/sunspec-certified-program/
and then email certification@sunspec.org to schedule your test.

## Index
Model | Label | Description | Notes
1 | Common | All SunSpec compliant devices must include this as the first model
2 | Basic Aggregator | Aggregates a collection of models for a given model id
3 | Secure Dataset Read Request | Request a digial signature over a specifed set of data registers | Used in conjunction witgh Secure Dataset Read Response Model
4 | Secure Dataset Read Response | Compute a digial signature over a specifed set of data registers
5 | Secure Write Request | Include a digial signature along with the control data
6 | Secure Write Sequential Request | Include a digial signature along with the control data
7 | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response | Used in conjunction with a Secure Write Request
8 | Get Device Security Certificate | Security model for PKI
9 | Set Operator Security Certificate | Security model for PKI
10 | Communication Interface Header | To be included first for a complete interface description
11 | Ethernet Link Layer | Include to support a wired ethernet port
12 | IPv4 | Include to support an IPv4 protocol stack on this interface
13 | IPv6 | Include to support an IPv6 protocol stack on this interface
14 | Proxy Server | Include this block to allow for a proxy server
15 | Interface Counters Model | Interface counters
16 | Simple IP Network | Include this model for a simple IPv4 network stack
17 | Serial Interface | Include this model for serial interface configuration support
18 | Cellular Link | Include this model to support a cellular interface link
19 | PPP Link | Include this model to configure a Point-to-Point Protocol link
101 | Inverter (Single Phase) | Include this model for single phase inverter monitoring
102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
103 | Inverter (Three Phase) | Include this model for three phase inverter monitoring
111 | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
112 | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
113 | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
120 | Nameplate | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
121 | Basic Settings | Inverter Controls Basic Settings | Ref 3: 8.4.2.1, Ref 4: 17
122 | Measurements_Status | Inverter Controls Extended Measurements and Status | Ref 3: 8.14.3.2, Ref 4: 17
123 | Immediate Controls | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
124 | Storage | Basic Storage Controls | Ref 3: 8.7.4.2
125 | Pricing | Pricing Signal | Ref 3: 8.7.5.1; Ref 4: 6
126 | Static Volt-VAR | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
127 | Freq-Watt Param | Parameterized Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
128 | Dynamic Reactive Current | Dynamic Reactive Current | Ref 3: 8.10.1.2; Ref 4: 12
129 | LVRTD | LVRT Must Disconnect | Ref 4: 11
130 | HVRTD | HVRT Must Disconnect | Ref 4: 11
131 | Watt-PF | Watt-Power Factor | Ref 3: 8.11.1.2
132 | Volt-Watt | Volt-Watt | Ref 3: 8.12.1.2
133 | Basic Scheduling | Basic Scheduling | Ref 2: 2.2.8
134 | Freq-Watt Crv | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
135 | LFRT | Low Frequency Ride-through | Ref 4: 11
136 | HFRT | High Frequency Ride-through | Ref 4: 11
137 | LVRTC | LVRT must remain connected | Ref 4: 11
138 | HVRTC | HVRT must remain connected | Ref 4: 11
160 | Multiple MPPT Inverter Extension Model
201 | Meter (Single Phase)single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
202 | split single phase (ABN) meter
203 | wye-connect three phase (abcn) meter
204 | delta-connect three phase (abc) meter
211 | single phase (AN or AB) meter |  | Float
212 | split single phase (ABN) meter |  | Float
213 | wye-connect three phase (abcn) meter |  | Float
214 | delta-connect three phase (abc) meter |  | Float
220 | Secure AC Meter Selected Readings | Include this model for secure metering
302 | Irradiance Model | Include to support various irradiance measurements
303 | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
304 | Inclinometer Model | Include to support orienation measurements
305 | GPS | Include to support location measurements
306 | Reference Point Model | Include to support a standard reference point
307 | Base Met | Base Meteorolgical Model | This model supersedes model 301
308 | Mini Met Model | Include to support a few basic measurements
401 | String Combiner (Current) | A basic string combiner | This model is SUPERSEDED by model 403
402 | String Combiner (Advanced) | An advanced string combiner | This model is SUPERSEDED by model 404
403 | String Combiner (Current) | A basic string combiner model | This model supersedes model 401
404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
501 | Solar Module | A solar module model supporing DC-DC converter | Float
502 | Solar Module | A solar module model supporing DC-DC converter | Integer
601 | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers | Trackers may include GPS model 305 for location information
801 | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
802 | Battery Base Model
803 | Lithium-Ion Battery Bank Model
804 | Lithium-Ion String Model
805 | Lithium-Ion Module Model
806 | Flow Battery Model
807 | Flow Battery String Model
808 | Flow Battery Module Model
809 | Flow Battery Stack Model
63001 | SunSpec Test Model 1
63002 | SunSpec Test Model 2
64001 | Veris Status and Configuration
64020 | Mersen GreenString
64101 | Eltek Inverter Extension
64110 | OutBack AXS device
64111 | Basic Charge Controller
64112 | OutBack FM Charge Controller

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | All SunSpec compliant devices must include this as the first model
Header |  | 1 |  | 1 | L |  | 65 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address

## 64401
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer System Model | 64401 | uint16 |  |  | R | M | Studer System Model
Header |  | 1 |  | 1 | L |  | 18 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | sysBatteryVoltage | Battery Voltage |  | float32 | V |  | R | O | {7000};If no BSP(601) present, get from 100 {3000}, if not present get from 300 {11000}, in not present get from 700 {15000}
Fixed Block |  | 4 | 2 | 2 | sysBatteryTemp | Battery Temperature |  | float32 | C |  | R | O | {7029};If no BSP(601) present, get from 100 {3001}, if not present get from 300 {11005}, in not present get from 700 {15032}
Fixed Block |  | 6 | 4 | 2 | sysBatteryCurrent | Battery Current |  | float32 | A |  | R | O | {7001};If no BSP present, add all Ibatt of all XT, VT & VS
Fixed Block |  | 8 | 6 | 2 | sysStateOfCharge | State of Charge |  | float32 | % |  | R | O | {7032};ONLY if BSP present
Fixed Block |  | 10 | 8 | 2 | sysChargedToday | Charged Today |  | float32 | Ah |  | R | O | {7007};ONLY if BSP present
Fixed Block |  | 12 | 10 | 2 | sysDischargedToday | Discharged Today |  | float32 | Ah |  | R | O | {7008};ONLY if BSP present
Fixed Block |  | 14 | 12 | 2 | sysPVPower | PV Power |  | float32 | W |  | R | O | {11004}+ {15010};Add PV power of all VarioTracks + VarioStrings
Fixed Block |  | 16 | 14 | 2 | sysPVChargingCurrent | PV Charging Current |  | float32 | A |  | R | O | {11001}+ {15001};Add battery current of all VarioTracks + VarioStrings
Fixed Block |  | 18 | 16 | 2 | sysPVEnergyToday | PV Energy Today |  | float32 | kWh |  | R | O | {11007}+ {15017};Add all daily production of alll VT + VS

## 64402
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer System Phase Value Model | 64402 | uint16 |  |  | R | M | Studer-Innotec System Phase Value Model
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 33) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | RB Count |  | 3 | uint16 |  |  | R | O | Number of Blocks (Phases)
Repeating Block |  | 3 | 0 | 1 | sysPhase | Phase | 0 | uint16 |  |  | R | O | Phase L1
Repeating Block |  | 4 | 1 | 2 | sysInVoltage | Input Voltage |  | float32 | V |  | R | O | 3113 [@191]
Repeating Block |  | 6 | 3 | 2 | sysInVoltageMin | Input Voltage Min |  | float32 | V |  | R | O | 3011 [@191]
Repeating Block |  | 8 | 5 | 2 | sysInVoltageMax | Input Voltage Max |  | float32 | V |  | R | O | 3012 [@191]
Repeating Block |  | 10 | 7 | 2 | sysInCurrent | Input Current |  | float32 | A |  | R | O | 3116 [@191]
Repeating Block |  | 12 | 9 | 2 | sysInCurrentMin | Input Current Min |  | float32 | A |  | R | O | 3114 [@191]
Repeating Block |  | 14 | 11 | 2 | sysInCurrentMax | Input Current Max |  | float32 | A |  | R | O | 3115 [@191]
Repeating Block |  | 16 | 13 | 2 | sysInFrequency | Input Frequency |  | float32 | Hz |  | R | O | 3122 [@191]
Repeating Block |  | 18 | 15 | 2 | sysInFrequencyMin | Input Frequency Min |  | float32 | Hz |  | R | O | 3120 [@191]
Repeating Block |  | 20 | 17 | 2 | sysInFrequencyMax | Input Frequency Max |  | float32 | Hz |  | R | O | 3121 [@191]
Repeating Block |  | 22 | 19 | 2 | sysInApparentPower | Input Power |  | float32 | kVA |  | R | O | 3013 [@191]
Repeating Block |  | 24 | 21 | 2 | sysInActivePower | Input Active Power |  | float32 | W |  | R | O | 3088 [@191]
Repeating Block |  | 26 | 23 | 2 | sysOutVoltage | Output Voltage |  | float32 | V |  | R | O | 3021 [@191]
Repeating Block |  | 28 | 25 | 2 | sysOutCurrent | Output Current |  | float32 | A |  | R | O | 3022 [@191]
Repeating Block |  | 30 | 27 | 2 | sysOutFrequency | Output Frequency |  | float32 | Hz |  | R | O | 3085 [@191]
Repeating Block |  | 32 | 29 | 2 | sysOutApparentPower | Output Power |  | float32 | kVA |  | R | O | 3023 [@191]
Repeating Block |  | 34 | 31 | 2 | sysOutActivePower | Output Active Power |  | float32 | W |  | R | O | 3087 [@191]
Repeating Block |  | 36 | 0 | 1 | sysPhase | Phase | 1 | uint16 |  |  | R | O | Phase L2
Repeating Block |  | 37 | 1 | 2 | sysInVoltage | Input Voltage |  | float32 | V |  | R | O | 3113 [@192]
Repeating Block |  | 39 | 3 | 2 | sysInVoltageMin | Input Voltage Min |  | float32 | V |  | R | O | 3011 [@192]
Repeating Block |  | 41 | 5 | 2 | sysInVoltageMax | Input Voltage Max |  | float32 | V |  | R | O | 3012 [@192]
Repeating Block |  | 43 | 7 | 2 | sysInCurrent | Input Current |  | float32 | A |  | R | O | 3116 [@192]
Repeating Block |  | 45 | 9 | 2 | sysInCurrentMin | Input Current Min |  | float32 | A |  | R | O | 3114 [@192]
Repeating Block |  | 47 | 11 | 2 | sysInCurrentMax | Input Current Max |  | float32 | A |  | R | O | 3115 [@192]
Repeating Block |  | 49 | 13 | 2 | sysInFrequency | Input Frequency |  | float32 | Hz |  | R | O | 3122 [@192]
Repeating Block |  | 51 | 15 | 2 | sysInFrequencyMin | Input Frequency Min |  | float32 | Hz |  | R | O | 3120 [@192]
Repeating Block |  | 53 | 17 | 2 | sysInFrequencyMax | Input Frequency Max |  | float32 | Hz |  | R | O | 3121 [@192]
Repeating Block |  | 55 | 19 | 2 | sysInApparentPower | Input Power |  | float32 | kVA |  | R | O | 3013 [@192]
Repeating Block |  | 57 | 21 | 2 | sysInActivePower | Input Active Power |  | float32 | W |  | R | O | 3088 [@192]
Repeating Block |  | 59 | 23 | 2 | sysOutVoltage | Output Voltage |  | float32 | V |  | R | O | 3021 [@192]
Repeating Block |  | 61 | 25 | 2 | sysOutCurrent | Output Current |  | float32 | A |  | R | O | 3022 [@192]
Repeating Block |  | 63 | 27 | 2 | sysOutFrequency | Output Frequency |  | float32 | Hz |  | R | O | 3085 [@192]
Repeating Block |  | 65 | 29 | 2 | sysOutApparentPower | Output Power |  | float32 | kVA |  | R | O | 3023 [@192]
Repeating Block |  | 67 | 31 | 2 | sysOutActivePower | Output Active Power |  | float32 | W |  | R | O | 3087 [@192]
Repeating Block |  | 69 | 0 | 1 | sysPhase | Phase | 2 | uint16 |  |  | R | O | Phase L3
Repeating Block |  | 70 | 1 | 2 | sysInVoltage | Input Voltage |  | float32 | V |  | R | O | 3113 [@193]
Repeating Block |  | 72 | 3 | 2 | sysInVoltageMin | Input Voltage Min |  | float32 | V |  | R | O | 3011 [@193]
Repeating Block |  | 74 | 5 | 2 | sysInVoltageMax | Input Voltage Max |  | float32 | V |  | R | O | 3012 [@193]
Repeating Block |  | 76 | 7 | 2 | sysInCurrent | Input Current |  | float32 | A |  | R | O | 3116 [@193]
Repeating Block |  | 78 | 9 | 2 | sysInCurrentMin | Input Current Min |  | float32 | A |  | R | O | 3114 [@193]
Repeating Block |  | 80 | 11 | 2 | sysInCurrentMax | Input Current Max |  | float32 | A |  | R | O | 3115 [@193]
Repeating Block |  | 82 | 13 | 2 | sysInFrequency | Input Frequency |  | float32 | Hz |  | R | O | 3122 [@193]
Repeating Block |  | 84 | 15 | 2 | sysInFrequencyMin | Input Frequency Min |  | float32 | Hz |  | R | O | 3120 [@193]
Repeating Block |  | 86 | 17 | 2 | sysInFrequencyMax | Input Frequency Max |  | float32 | Hz |  | R | O | 3121 [@193]
Repeating Block |  | 88 | 19 | 2 | sysInApparentPower | Input Power |  | float32 | kVA |  | R | O | 3013 [@193]
Repeating Block |  | 90 | 21 | 2 | sysInActivePower | Input Active Power |  | float32 | W |  | R | O | 3088 [@193]
Repeating Block |  | 92 | 23 | 2 | sysOutVoltage | Output Voltage |  | float32 | V |  | R | O | 3021 [@193]
Repeating Block |  | 94 | 25 | 2 | sysOutCurrent | Output Current |  | float32 | A |  | R | O | 3022 [@193]
Repeating Block |  | 96 | 27 | 2 | sysOutFrequency | Output Frequency |  | float32 | Hz |  | R | O | 3085 [@193]
Repeating Block |  | 98 | 29 | 2 | sysOutApparentPower | Output Power |  | float32 | kVA |  | R | O | 3023 [@193]
Repeating Block |  | 100 | 31 | 2 | sysOutActivePower | Output Active Power |  | float32 | W |  | R | O | 3087 [@193]

## 64403
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer Event Model | 64403 | uint16 |  |  | R | M | Studer-Innotec Event Model
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 5) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | RB Count |  | 10 | uint16 |  |  | R | O | Number of Blocks
Repeating Block |  | 3 | 1 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 5 | 3 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 7 | 5 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 8 | 6 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 10 | 8 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 12 | 10 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 13 | 11 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 15 | 13 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 17 | 15 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 18 | 16 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 20 | 18 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 22 | 20 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 23 | 21 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 25 | 23 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 27 | 25 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 28 | 26 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 30 | 28 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 32 | 30 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 33 | 31 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 35 | 33 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 37 | 35 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 38 | 36 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 40 | 38 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 42 | 40 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 43 | 41 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 45 | 43 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 47 | 45 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 48 | 46 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 50 | 48 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 52 | 50 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
enum16 | evtMsgType |  |  | Name: msg0; Label: Warning (000): Battery low; Value: 0
enum16 | evtMsgType |  |  | Name: msg1; Label: Warning (001): Battery too high; Value: 1
enum16 | evtMsgType |  |  | Name: msg2; Label: Warning (002): Bulk charge too long; Value: 2
enum16 | evtMsgType |  |  | Name: msg3; Label: (003): AC-In synchronization in progress; Value: 3
enum16 | evtMsgType |  |  | Name: msg4; Label: Warning (004): Input frequency AC-In wrong; Value: 4
enum16 | evtMsgType |  |  | Name: msg5; Label: Warning (005): Input frequency AC-In wrong; Value: 5
enum16 | evtMsgType |  |  | Name: msg6; Label: Warning (006): Input voltage AC-In too high; Value: 6
enum16 | evtMsgType |  |  | Name: msg7; Label: Warning (007): Input voltage AC-In too low; Value: 7
enum16 | evtMsgType |  |  | Name: msg8; Label: Halted (008): Inverter overload SC; Value: 8
enum16 | evtMsgType |  |  | Name: msg9; Label: Halted (009): Charger short circuit; Value: 9
enum16 | evtMsgType |  |  | Name: msg10; Label: (010): System start-up in progress; Value: 10
enum16 | evtMsgType |  |  | Name: msg11; Label: Warning (011): AC-In Energy quota; Value: 11
enum16 | evtMsgType |  |  | Name: msg12; Label: (012): Use of battery temperature sensor; Value: 12
enum16 | evtMsgType |  |  | Name: msg13; Label: (013): Use of additional remote control; Value: 13
enum16 | evtMsgType |  |  | Name: msg14; Label: Halted (014): Over temperature EL; Value: 14
enum16 | evtMsgType |  |  | Name: msg15; Label: Halted (015): Inverter overload BL; Value: 15
enum16 | evtMsgType |  |  | Name: msg16; Label: Warning (016): Fan error detected; Value: 16
enum16 | evtMsgType |  |  | Name: msg17; Label: (017): Programing mode; Value: 17
enum16 | evtMsgType |  |  | Name: msg18; Label: Warning (018): Excessive battery voltage ripple; Value: 18
enum16 | evtMsgType |  |  | Name: msg19; Label: Halted (019): Battery undervoltage; Value: 19
enum16 | evtMsgType |  |  | Name: msg20; Label: Halted (020): Battery overvoltage; Value: 20
enum16 | evtMsgType |  |  | Name: msg21; Label: (021): Transfer not authorized, AC-Out current is higher than {1107}; Value: 21
enum16 | evtMsgType |  |  | Name: msg22; Label: Halted (022): Voltage presence on AC-Out; Value: 22
enum16 | evtMsgType |  |  | Name: msg23; Label: Halted (023): Phase not defined; Value: 23
enum16 | evtMsgType |  |  | Name: msg24; Label: Warning (024): Change the clock battery; Value: 24
enum16 | evtMsgType |  |  | Name: msg25; Label: Halted (025): Unknown Command board. Software upgrade needed; Value: 25
enum16 | evtMsgType |  |  | Name: msg26; Label: Halted (026): Unknown Power board. Software upgrade needed; Value: 26
enum16 | evtMsgType |  |  | Name: msg27; Label: Halted (027): Unknown extension board. Software upgrade needed; Value: 27
enum16 | evtMsgType |  |  | Name: msg28; Label: Halted (028): Voltage incompatibility Power - Command; Value: 28
enum16 | evtMsgType |  |  | Name: msg29; Label: Halted (029): Voltage incompatibility Ext. - Command; Value: 29
enum16 | evtMsgType |  |  | Name: msg30; Label: Halted (030): Power incompatibility Power - Command; Value: 30
enum16 | evtMsgType |  |  | Name: msg31; Label: Halted (031): Command board software incompatibility; Value: 31
enum16 | evtMsgType |  |  | Name: msg32; Label: Halted (032): Power board software incompatibility; Value: 32
enum16 | evtMsgType |  |  | Name: msg33; Label: Halted (033): Extension board software incompatibility; Value: 33
enum16 | evtMsgType |  |  | Name: msg34; Label: Halted (034): FID corruption, call factory; Value: 34
enum16 | evtMsgType |  |  | Name: msg35; Label: (035): Memory structure modified; Value: 35
enum16 | evtMsgType |  |  | Name: msg36; Label: Halted (036): Parameter file lacking; Value: 36
enum16 | evtMsgType |  |  | Name: msg37; Label: Warning (037): Message file lack. SW upgrade advised; Value: 37
enum16 | evtMsgType |  |  | Name: msg38; Label: Warning (038): Upgrade of the device software advised; Value: 38
enum16 | evtMsgType |  |  | Name: msg39; Label: Warning (039): Upgrade of the device software advised; Value: 39
enum16 | evtMsgType |  |  | Name: msg40; Label: Warning (040): Upgrade of the device software advised; Value: 40
enum16 | evtMsgType |  |  | Name: msg41; Label: Warning (041): Over temperature TR; Value: 41
enum16 | evtMsgType |  |  | Name: msg42; Label: Halted (042): Unauthorized energy source at the output; Value: 42
enum16 | evtMsgType |  |  | Name: msg43; Label: (043): Start of monthly test; Value: 43
enum16 | evtMsgType |  |  | Name: msg44; Label: (044): End of successfully monthly test; Value: 44
enum16 | evtMsgType |  |  | Name: msg45; Label: Warning (045): Monthly autonomy test failed; Value: 45
enum16 | evtMsgType |  |  | Name: msg46; Label: (046): Start of weekly test; Value: 46
enum16 | evtMsgType |  |  | Name: msg47; Label: (047): End of successfully weekly test; Value: 47
enum16 | evtMsgType |  |  | Name: msg48; Label: Warning (048): Weekly autonomy test failed; Value: 48
enum16 | evtMsgType |  |  | Name: msg49; Label: (049): Transfer opened because AC-In max current exceeded {1107}; Value: 49
enum16 | evtMsgType |  |  | Name: msg50; Label: Error (050): Incomplete data transfer; Value: 50
enum16 | evtMsgType |  |  | Name: msg51; Label: (051): The update is finished; Value: 51
enum16 | evtMsgType |  |  | Name: msg52; Label: (052): Your installation is already updated; Value: 52
enum16 | evtMsgType |  |  | Name: msg53; Label: Halted (053): Devices not compatible, software update required; Value: 53
enum16 | evtMsgType |  |  | Name: msg54; Label: (054): Please wait. Data transfer in progress; Value: 54
enum16 | evtMsgType |  |  | Name: msg55; Label: Error (055): No SD card inserted; Value: 55
enum16 | evtMsgType |  |  | Name: msg56; Label: Warning (056): Upgrade of the RCC software advised; Value: 56
enum16 | evtMsgType |  |  | Name: msg57; Label: (057): Operation finished successfully; Value: 57
enum16 | evtMsgType |  |  | Name: msg58; Label: Halted (058): Master synchronization missing; Value: 58
enum16 | evtMsgType |  |  | Name: msg59; Label: Halted (059): Inverter overload HW; Value: 59
enum16 | evtMsgType |  |  | Name: msg60; Label: Warning (060): Time security 1512 AUX1; Value: 60
enum16 | evtMsgType |  |  | Name: msg61; Label: Warning (061): Time security 1513 AUX2; Value: 61
enum16 | evtMsgType |  |  | Name: msg62; Label: Warning (062): Genset, no AC-In coming after AUX command; Value: 62
enum16 | evtMsgType |  |  | Name: msg63; Label: (063): Save parameter XT; Value: 63
enum16 | evtMsgType |  |  | Name: msg64; Label: (064): Save parameter BSP; Value: 64
enum16 | evtMsgType |  |  | Name: msg65; Label: (065): Save parameter VarioTrack; Value: 65
enum16 | evtMsgType |  |  | Name: msg71; Label: Error (071): Insufficient disk space on SD card; Value: 71
enum16 | evtMsgType |  |  | Name: msg72; Label: Halted (072): COM identification incorrect; Value: 72
enum16 | evtMsgType |  |  | Name: msg73; Label: (073): Datalogger is enabled on this RCC; Value: 73
enum16 | evtMsgType |  |  | Name: msg74; Label: (074): Save parameter Xcom-MS; Value: 74
enum16 | evtMsgType |  |  | Name: msg75; Label: (075): MPPT MS address changed successfully; Value: 75
enum16 | evtMsgType |  |  | Name: msg76; Label: Error (076): Error during change of MPPT MS address; Value: 76
enum16 | evtMsgType |  |  | Name: msg77; Label: Error (077): Wrong MPPT MS DIP Switch position; Value: 77
enum16 | evtMsgType |  |  | Name: msg78; Label: (078): SMS or email sent; Value: 78
enum16 | evtMsgType |  |  | Name: msg79; Label: Halted (079): More than 9 XTs in the system; Value: 79
enum16 | evtMsgType |  |  | Name: msg80; Label: Halted (080): No battery (or reverse polarity); Value: 80
enum16 | evtMsgType |  |  | Name: msg81; Label: Warning (081): Earthing fault; Value: 81
enum16 | evtMsgType |  |  | Name: msg82; Label: Halted (082): PV overvoltage; Value: 82
enum16 | evtMsgType |  |  | Name: msg83; Label: Warning (083): No solar production in the last 48h; Value: 83
enum16 | evtMsgType |  |  | Name: msg84; Label: (084): Equalization performed; Value: 84
enum16 | evtMsgType |  |  | Name: msg85; Label: Error (085): Modem not available; Value: 85
enum16 | evtMsgType |  |  | Name: msg86; Label: Error (086): Incorrect PIN code, unable to initiate the modem; Value: 86
enum16 | evtMsgType |  |  | Name: msg87; Label: Error (087): Insufficient Signal from GSM modem; Value: 87
enum16 | evtMsgType |  |  | Name: msg88; Label: Error (088): No connection to GSM network; Value: 88
enum16 | evtMsgType |  |  | Name: msg89; Label: Error (089): No server access; Value: 89
enum16 | evtMsgType |  |  | Name: msg90; Label: (090): Server connected; Value: 90
enum16 | evtMsgType |  |  | Name: msg91; Label: Error (091): Update software of other RCC or Xcom-232i; Value: 91
enum16 | evtMsgType |  |  | Name: msg92; Label: Error (092): More than 3 RCC or Xcom-232i in the system; Value: 92
enum16 | evtMsgType |  |  | Name: msg93; Label: Error (093): More than 1 BSP in the system; Value: 93
enum16 | evtMsgType |  |  | Name: msg94; Label: Error (094): More than 1 Xcom-MS in the system; Value: 94
enum16 | evtMsgType |  |  | Name: msg95; Label: Error (095): More than 15 VarioTrack in the system; Value: 95
enum16 | evtMsgType |  |  | Name: msg121; Label: Error (121): Impossible communication with target device; Value: 121
enum16 | evtMsgType |  |  | Name: msg122; Label: Error (122): SD card corrupted; Value: 122
enum16 | evtMsgType |  |  | Name: msg123; Label: Error (123): SD card not formatted; Value: 123
enum16 | evtMsgType |  |  | Name: msg124; Label: Error (124): SD card not compatible; Value: 124
enum16 | evtMsgType |  |  | Name: msg125; Label: Error (125): SD card format not recognized. Should be FAT; Value: 125
enum16 | evtMsgType |  |  | Name: msg126; Label: Error (126): SD card write protected; Value: 126
enum16 | evtMsgType |  |  | Name: msg127; Label: Error (127): SD card, file(s) corrupted; Value: 127
enum16 | evtMsgType |  |  | Name: msg128; Label: Error (128): SD card file or directory could not be found; Value: 128
enum16 | evtMsgType |  |  | Name: msg129; Label: Error (129): SD card has been prematurely removed; Value: 129
enum16 | evtMsgType |  |  | Name: msg130; Label: Error (130): Update directory is empty; Value: 130
enum16 | evtMsgType |  |  | Name: msg131; Label: (131): The VarioTrack is configured for 12V batteries; Value: 131
enum16 | evtMsgType |  |  | Name: msg132; Label: (132): The VarioTrack is configured for 24V batteries; Value: 132
enum16 | evtMsgType |  |  | Name: msg133; Label: (133): The VarioTrack is configured for 48V batteries; Value: 133
enum16 | evtMsgType |  |  | Name: msg134; Label: (134): Reception level of the GSM signal; Value: 134
enum16 | evtMsgType |  |  | Name: msg137; Label: (137): VarioTrack master synchronization lost; Value: 137
enum16 | evtMsgType |  |  | Name: msg138; Label: Error (138): XT master synchronization lost; Value: 138
enum16 | evtMsgType |  |  | Name: msg139; Label: (139): Synchronized on VarioTrack master; Value: 139
enum16 | evtMsgType |  |  | Name: msg140; Label: (140): Synchronized on XT master; Value: 140
enum16 | evtMsgType |  |  | Name: msg141; Label: Error (141): More than 1 Xcom-SMS in the system; Value: 141
enum16 | evtMsgType |  |  | Name: msg142; Label: Error (142): More than 15 VarioString in the system; Value: 142
enum16 | evtMsgType |  |  | Name: msg143; Label: (143): Save parameter Xcom-SMS; Value: 143
enum16 | evtMsgType |  |  | Name: msg144; Label: (144): Save parameter VarioString; Value: 144
enum16 | evtMsgType |  |  | Name: msg145; Label: Error (145): SIM card blocked, PUK code required; Value: 145
enum16 | evtMsgType |  |  | Name: msg146; Label: Error (146): SIM card missing; Value: 146
enum16 | evtMsgType |  |  | Name: msg147; Label: Error (147): Install R532 firmware release prior to install an older release; Value: 147
enum16 | evtMsgType |  |  | Name: msg148; Label: (148): Datalogger function interrupted (SD card removed); Value: 148
enum16 | evtMsgType |  |  | Name: msg149; Label: Error (149): Parameter setting incomplete; Value: 149
enum16 | evtMsgType |  |  | Name: msg150; Label: Error (150): Cabling error between PV and VarioString; Value: 150
enum16 | evtMsgType |  |  | Name: msg162; Label: Error (162): Communication loss with RCC or Xcom-232i; Value: 162
enum16 | evtMsgType |  |  | Name: msg163; Label: Error (163): Communication loss with Xtender; Value: 163
enum16 | evtMsgType |  |  | Name: msg164; Label: Error (164): Communication loss with BSP; Value: 164
enum16 | evtMsgType |  |  | Name: msg165; Label: Error (165): Communication loss with Xcom-MS; Value: 165
enum16 | evtMsgType |  |  | Name: msg166; Label: Error (166): Communication loss with VarioTrack; Value: 166
enum16 | evtMsgType |  |  | Name: msg167; Label: Error (167): Communication loss with VarioString; Value: 167
enum16 | evtMsgType |  |  | Name: msg168; Label: (168): Synchronized with VarioString master; Value: 168
enum16 | evtMsgType |  |  | Name: msg169; Label: (169): Synchronization with VarioString master lost; Value: 169
enum16 | evtMsgType |  |  | Name: msg170; Label: Warning (170): No solar production in the last 48h on PV1; Value: 170
enum16 | evtMsgType |  |  | Name: msg171; Label: Warning (171): No solar production in the last 48h on PV2; Value: 171
enum16 | evtMsgType |  |  | Name: msg172; Label: Error (172): FID change impossible. More than one unit.; Value: 172
enum16 | evtMsgType |  |  | Name: msg173; Label: Error (173): Incompatible Xtender. Please contact Studer Innotec SA; Value: 173
enum16 | evtMsgType |  |  | Name: msg174; Label: (174): Inaccessible parameter, managed by the Xcom-CAN; Value: 174
enum16 | evtMsgType |  |  | Name: msg175; Label: Halted (175): Critical undervoltage; Value: 175
enum16 | evtMsgType |  |  | Name: msg176; Label: (176): Calibration setting lost; Value: 176
enum16 | evtMsgType |  |  | Name: msg177; Label: (177): An Xtender has started up; Value: 177
enum16 | evtMsgType |  |  | Name: msg178; Label: (178): No BSP. Necessary for programming with SOC; Value: 178
enum16 | evtMsgType |  |  | Name: msg179; Label: (179): No BTS or BSP. Necessary for programming with temperature; Value: 179
enum16 | evtMsgType |  |  | Name: msg180; Label: (180): Command entry activated; Value: 180
enum16 | evtMsgType |  |  | Name: msg181; Label: Error (181): Disconnection of BTS; Value: 181
enum16 | evtMsgType |  |  | Name: msg182; Label: (182): BTS/BSP battery temperature measurement used by a device; Value: 182
enum16 | evtMsgType |  |  | Name: msg183; Label: Halted (183): An Xtender has lost communication with the system; Value: 183
enum16 | evtMsgType |  |  | Name: msg184; Label: Error (184): Check phase orientation or circuit breakers state on AC-In; Value: 184
enum16 | evtMsgType |  |  | Name: msg185; Label: Warning (185): AC-In voltage level with delay too low; Value: 185
enum16 | evtMsgType |  |  | Name: msg186; Label: Halted (186): Critical undervoltage (fast); Value: 186
enum16 | evtMsgType |  |  | Name: msg187; Label: Halted (187): Critical overvoltage (fast); Value: 187
enum16 | evtMsgType |  |  | Name: msg188; Label: (188): CAN stage startup; Value: 188
enum16 | evtMsgType |  |  | Name: msg189; Label: Error (189): Incompatible configuration file; Value: 189
enum16 | evtMsgType |  |  | Name: msg190; Label: (190): The Xcom-SMS is busy; Value: 190
enum16 | evtMsgType |  |  | Name: msg191; Label: (191): Parameter not supported; Value: 191
enum16 | evtMsgType |  |  | Name: msg192; Label: (192): Unknown reference; Value: 192
enum16 | evtMsgType |  |  | Name: msg193; Label: (193): Invalid value; Value: 193
enum16 | evtMsgType |  |  | Name: msg194; Label: (194): Value too low; Value: 194
enum16 | evtMsgType |  |  | Name: msg195; Label: (195): Value too high; Value: 195
enum16 | evtMsgType |  |  | Name: msg196; Label: (196): Writing error; Value: 196
enum16 | evtMsgType |  |  | Name: msg197; Label: (197): Reading error; Value: 197
enum16 | evtMsgType |  |  | Name: msg198; Label: (198): User level insufficient; Value: 198
enum16 | evtMsgType |  |  | Name: msg199; Label: (199): No data for the report; Value: 199
enum16 | evtMsgType |  |  | Name: msg200; Label: Error (200): Memory full; Value: 200
enum16 | evtMsgType |  |  | Name: msg202; Label: Warning (202): External alarm arrives; Value: 202
enum16 | evtMsgType |  |  | Name: msg203; Label: (203): External alarm leaves; Value: 203
enum16 | evtMsgType |  |  | Name: msg204; Label: Error (204): External stop arrives; Value: 204
enum16 | evtMsgType |  |  | Name: msg205; Label: (205): External stop leaves; Value: 205
enum16 | evtMsgType |  |  | Name: msg206; Label: Halted (206): Board hardware incompatibility; Value: 206
enum16 | evtMsgType |  |  | Name: msg207; Label: (207): AUX1 relay activation; Value: 207
enum16 | evtMsgType |  |  | Name: msg208; Label: (208): AUX1 relay deactivation; Value: 208
enum16 | evtMsgType |  |  | Name: msg209; Label: (209): AUX2 relay activation; Value: 209
enum16 | evtMsgType |  |  | Name: msg210; Label: (210): AUX2 relay deactivation; Value: 210
enum16 | evtMsgType |  |  | Name: msg211; Label: (211): Command entry deactivated; Value: 211
enum16 | evtMsgType |  |  | Name: msg212; Label: Error (212): VarioTrack software incompatibility. Upgrade needed; Value: 212
enum16 | evtMsgType |  |  | Name: msg213; Label: (213): Battery current limitation by the BSP stopped; Value: 213
enum16 | evtMsgType |  |  | Name: msg214; Label: Warning (214): Half period RMS voltage limit exceeded, transfer opened; Value: 214
enum16 | evtMsgType |  |  | Name: msg215; Label: Warning (215): UPS limit reached, transfer opened; Value: 215
enum16 | evtMsgType |  |  | Name: msg216; Label: Warning (216): Scom watchdog caused the reset of Xcom-232i; Value: 216
enum16 | evtMsgType |  |  | Name: msg217; Label: Warning (217): CAN problem at Xtender declaration; Value: 217
enum16 | evtMsgType |  |  | Name: msg218; Label: Warning (218): CAN problem while writing parameters; Value: 218
enum16 | evtMsgType |  |  | Name: msg222; Label: (222): Front ON/OFF button pressed; Value: 222
enum16 | evtMsgType |  |  | Name: msg223; Label: (223): Main OFF detected; Value: 223
enum16 | evtMsgType |  |  | Name: msg224; Label: (224): Delay before closing transfer relay in progress {1580}; Value: 224
enum16 | evtMsgType |  |  | Name: msg225; Label: Error (225): Communication with lithium battery lost; Value: 225
enum16 | evtMsgType |  |  | Name: msg226; Label: (226): Communication with lithium battery restored; Value: 226