## License Agreement
SunSpec Alliance
SunSpec Infomation Model Reference
Date Generated: 2021-12-09
This document is generated programatically from the canonical model definitions contained in the SunSpec model repository.
For the most up-to-date version of this document, go to: https://sunspec.org/sunspec-specifications/
Copyright SunSpec Alliance 2009-2021. All Rights Reserved.
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy. The complete policy of the SunSpec Alliance can be found at www.sunspec.org.
Prepared by the SunSpec Alliance
4040 Moorpark Avenue Suite 110
San Jose, CA 95117
Website: www.sunspec.org
Email: info@sunspec.org

## Summary
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter (superseded by the 700 series)
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | DER
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is programmatically generated from SunSpec model definition files, which can be downloaded from:
https://github.com/sunspec/models
Please note that the SunSpec model definition files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at:
https://sunspec.org/sunspec-specifications/
SunSpec Certification
If you would like to have your product SunSpec Certified you can apply for Certification here:
https://sunspec.org/sunspec-certification-application/
After applying, someone from SunSpec will followup shortly.
You can also contact certification@sunspec.org to ask questions and start the process.

## Change Log
Date | Issue # | Models | Change
12-09-21
| 229 | 714 | Added units
| 230 | 714 | Added Tmp_SF as scale factor
| 231 | 705 - 708 | Updated VRefPct unit label to VNomPct to clarify usage, this update does not change the functional behavior, just clarifies the reference source.
07-08-21
| 221 | 704, 705 | Removed Power Priority enums IEEE_1547, PF
| 224 | 704 | To point VarSetMod added enum VA_MAX_PCT
06-01-21
|  | 701 | Changed all power factor points to signed
|  | 701 | For point InvSt changed symbol "MPPT" to "RUNNING"
04-23-21
|  | 713 | Updated Model Length
04-16-21
|  | 713 | Added SF 'Pct_SF', assigned SF to points SoC, SoH
|  | 711 | Fixed labels and descriptions
04-15-21
|  | 700 series | Updated labels and descriptions. Fixed typos.
|  | 700 series | Removed notes attribute.
03-02-21
| 197 |  | Updated JSON schema
| 201 | 705-712 | Made ReadOnly point Mandatory and Static
| 198 | All models | Added size to all points in all models. Size is now mandatory.
|  | All models | Updated JSON schema to make "size" required on point object
| 199 | 701-715 | Made ID, L, and Ena point labels consistent
| 162 |  | Added symbols to point schema
| 205 | 705-712 | Fixed labels on Ena point
| 200 | 711 | Added point 'PMin'
| 34 | 803 | Changed point 'ModTmpAvg' type to 'int16'
01-21-21
| 195 | 702 | Made all read-only points Static
| 194 | 1 | Made all points except DA Static
| 193 | 704 | Changed point naming 'xxxRvrtEna' to 'xxxEnaRvrt'
| 181 | 802 | Fixed description for point 'SoCRsvMin'
| 192 | 16 | Changed 'Ctl' point type to 'bitfield16'
01-13-21
| 190 | 705 | Model 705; For points 'VRef', 'VRefAuto' added sf 'V_SF' and units 'VRefPct'
01-12-21
| 187 | 715 | Fixed incorrect model length
01-11-21
| 184 | All 700 | All enums now use 0 based indexing
| 163 | 715 | Update points 'DERHb', 'ControllerHb' type to uint32
| 185, 180 | 701, 702, 703, 704, 713, 715 | Added model lengths
| 179 | 701 | Fixed typo
12-14-20
| 177 | 714 | Updated point 'DCSt' to 'DCSta'
| 176 | 713 | Added point 'St'
| 175 | 701, 702 | Fixed numbering on symbols for points 'ThrottSrc' and 'CtrlModes'
| 174 | 704 | Added point 'AntiIslEna'
| 173 | 713 | Reordered points
12-04-20
| 171 | 701 | Changed point 'ACType' to Mandatory
12-03-20
| 158 | 707-710 | Fixed typo in description
| 159 | 712 | Changed point 'Pri' access to 'RW'
| 164 | 701 | Changed points with units 'V' to type 'uint16'
| 165 | 703 | Added point 'ESDlyRemTms'
| 166 | 701 | Removed symbols from point St, added point DERMode
| 167 | All 700 | Capitalized word 'id' in labels and descriptions
| 168 | 713, 714, 715 | Created new 713, incremented old 713, 714
11-05-20
| 154 | 704, 705, 706, 712 | Changed point type to int16 for points: (704) 'WSetPct', 'WSetPctRvrt', 'VarSetPct', 'VarSetPctRvrt'; (705) 'Var'; (706) 'W'; (712) 'W', 'Var'
| 155 | 701 | Added point 'InvSt'
| 153 | 701 | Removed notes
| 156 | 714 | Added model 714
10-30-20
| 141 | 701, 703, 704, 705, 706, 709, 710, 711, 712 | Update to make Point type and units consistent across models
| 119 | 702 | Add symbols to points 'IntIslandCatRtg', 'IntIslandCat
| 151 | 702 | Adds points 'PFOvrExt' and 'PFUndExt'
| 150 | 704 | Changed point names 'RGra' -> 'WRmp' and 'RGraRef' -> 'WRmpRef
| 147 | 704 | Add 'Pct' to 'WMaxLim' points, updated labels
| 149 | 705, 712 | Add symbol 'VA_MAX_PCT' to point 'DeptRef'
| 150 | 704 | Add point 'VarRmp'
| 144 | 702 | Update point 'Vnom' to 'VNom'
| 146 | 701 | Update PF points type to uint16
| 148 | 701 | Change point 'VL3N' to 'VL3'
| 145 | 705-712 | Remove CrvSt point
| 142 | 711 | Adds label to 'Ena' point
| 139 | 702 | Changed point 'IntIslandCatRtg' access to ReadOnly
| 134 | 707, 708, 709, 710 | Tms point type changed to uint32, Freq point renamed to Hz
| 130 | 705, 706 | Added RspTms_SF point
| 124 | 705 | Changed point name 'VRefTms' to 'VRefAutoTms'
09-17-20
| 131 | 712 | Changed 'W' point type to 'int16'
|  | All 700 series | Capitalized labels
| 129 | 711 | Added ReadOnly point to Controls
| 127 | 706 | fixed incorrect description for 'W' point
| 125 | 701 | Changed 'Hz' point type to uint32
| 122 | 705 | Changed Pri point to RW
| 121 | 704 | Set VarSetPri to RW
| 117 | 711 | Changed point names to use control naming
| 115 | 701 | Changed abbreviation of "Manufacturer" to "Mn"
| 116 | 704 | changed all reversion enables to read-write
09-03-20
| 112 | 705 | added VRefAutoEna and updated VRefAuto
| 110 | 702 | changed symbol names for the CtrlModes point to use '_TRIP' instead of 'RT'
| 113 | 702 | Removed VRefOfs point
| 114 | 702 | Reordered the order of the settings points to match the order of the ratings points
Updated schema.json to include the "notes" property
| 109 |  | Removed Detail Description, replaced with Notes
08-03-20
| 101 | 713 | Added symbols to the DCSt point
| 107 | 704 | Fix reversion enable functionality
| 102 | 704 | added RGraRef point
| 96 | 101 | fixed wrong sf name for points: TotVarhInj and TotVarhAbs
| 103 | 713 | fixed Tmp point detail description typo
| 100 | 707 | fixed NCrvSet misspelling
06-03-20
| 89 | 707, 708, 709, 710 | Added ReadOnly point to Crv group with access set to R
| 94 | 707, 708, 709, 710 | Changed curve points access to RW
| 93 | 705, 706, 707, 708, 709, 710, 712 | Changed curve points mandatory to optional
| 95 | 703 | Changed L access to R
| 92 | 705 | Changed VRefAuto type to enum16, added DISABLED 0 as enumeration
| 91 | 707, 708, 709, 710 | Added enumeration values for CrvSt
| 90 | 705, 706 | Changed ReadOnly access to R
| 88 | 707, 708, 709, 710 | Changed ActPt access to RW
| 87 | 707, 708, 709, 710 | Changed name of NCrv to NCrvSet

## Index
Model | Label | Description
1 | Common | All SunSpec compliant devices must include this as the first model
2 | Basic Aggregator | Aggregates a collection of models for a given model id
3 | Secure Dataset Read Request | Request a digital signature over a specified set of data registers
4 | Secure Dataset Read Response | Compute a digital signature over a specified set of data registers
5 | Secure Write Request | Include a digital signature along with the control data
6 | Secure Write Sequential Request | Include a digital signature along with the control data
7 | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response
8 | Get Device Security Certificate | Security model for PKI
9 | Set Operator Security Certificate | Security model for PKI
10 | Communication Interface Header | To be included first for a complete interface description
11 | Ethernet Link Layer | Include to support a wired ethernet port
12 | IPv4 | Include to support an IPv4 protocol stack on this interface
13 | IPv6 | Include to support an IPv6 protocol stack on this interface
14 | Proxy Server | Include this block to allow for a proxy server
15 | Interface Counters Model | Interface counters
16 | Simple IP Network | Include this model for a simple IPv4 network stack
17 | Serial Interface | Include this model for serial interface configuration support
18 | Cellular Link | Include this model to support a cellular interface link
19 | PPP Link | Include this model to configure a Point-to-Point Protocol link
101 | Inverter (Single Phase) | Include this model for single phase inverter monitoring
102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
103 | Inverter (Three Phase) | Include this model for three phase inverter monitoring
111 | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
112 | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
113 | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
120 | Nameplate | Inverter Controls Nameplate Ratings
121 | Basic Settings | Inverter Controls Basic Settings
122 | Measurements_Status | Inverter Controls Extended Measurements and Status
123 | Immediate Controls | Immediate Inverter Controls
124 | Storage | Basic Storage Controls
125 | Pricing | Pricing Signal
126 | Static Volt-VAR | Static Volt-VAR Arrays
127 | Freq-Watt Param | Parameterized Frequency-Watt
128 | Dynamic Reactive Current | Dynamic Reactive Current
129 | LVRTD | LVRT Must Disconnect
130 | HVRTD | HVRT Must Disconnect
131 | Watt-PF | Watt-Power Factor
132 | Volt-Watt | Volt-Watt
133 | Basic Scheduling | Basic Scheduling
134 | Freq-Watt Crv | Curve-Based Frequency-Watt
135 | LFRT | Low Frequency Ride-through
136 | HFRT | High Frequency Ride-through
137 | LVRTC | LVRT must remain connected
138 | HVRTC | HVRT must remain connected
139 | LVRTX | LVRT extended curve
140 | HVRTX | HVRT extended curve
141 | LFRTC | LFRT must remain connected
142 | HFRTC | HFRT must remain connected
143 | LFRTX | LFRT extended curve
144 | HFRTX | HFRT extended curve
145 | Extended Settings | Inverter controls extended settings
160 | Multiple MPPT Inverter Extension Model
201 | Meter (Single Phase)single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
202 | split single phase (ABN) meter
203 | wye-connect three phase (abcn) meter
204 | delta-connect three phase (abc) meter
211 | single phase (AN or AB) meter
212 | split single phase (ABN) meter
213 | wye-connect three phase (abcn) meter
214 | delta-connect three phase (abc) meter
220 | Secure AC Meter Selected Readings | Include this model for secure metering
302 | Irradiance Model | Include to support various irradiance measurements
303 | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
304 | Inclinometer Model | Include to support orientation measurements
305 | GPS | Include to support location measurements
306 | Reference Point Model | Include to support a standard reference point
307 | Base Met | Base Meteorological Model
308 | Mini Met Model | Include to support a few basic measurements
401 | String Combiner (Current) | A basic string combiner
402 | String Combiner (Advanced) | An advanced string combiner
403 | String Combiner (Current) | A basic string combiner model
404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements
501 | Solar Module | A solar module model supporting DC-DC converter
502 | Solar Module | A solar module model supporting DC-DC converter
601 | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers
701 | DER AC Measurement | DER AC measurement model.
702 | DER Capacity | DER capacity model.
703 | Enter Service | Enter service model.
704 | DER AC Controls | DER AC controls model.
705 | DER Volt-Var | DER Volt-Var model.
706 | DER Volt-Watt | DER Volt-Watt model.
707 | DER Trip LV | DER low voltage trip model.
708 | DER Trip HV | DER high voltage trip model.
709 | DER Trip LF | DER low frequency trip model.
710 | DER Trip HF | DER high frequency trip model.
711 | DER Frequency Droop | DER Frequency Droop model.
712 | DER Watt-Var | DER Watt-Var model.
713 | DER Storage Capacity | DER storage capacity.
714 | DER DC Measurement | DER DC measurement.
715 | DERCtl | DER Control
801 | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
802 | Battery Base Model
803 | Lithium-Ion Battery Bank Model
804 | Lithium-Ion String Model
805 | Lithium-Ion Module Model
806 | Flow Battery Model
807 | Flow Battery String Model
808 | Flow Battery Module Model
809 | Flow Battery Stack Model
63001 | SunSpec Test Model 1
63002 | SunSpec Test Model 2
64001 | Veris Status and Configuration
64020 | Mersen GreenString
64101 | Eltek Inverter Extension
64110 | OutBack AXS device
64111 | Basic Charge Controller
64112 | OutBack FM Charge Controller

## 1
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | common |  |  | group | [6 empty] | Common | All SunSpec compliant devices must include this as the first model
0 |  | ID | 1 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L | 65 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Mn |  |  | string | 16 |  |  |  | M | S | Manufacturer | Well known value registered with SunSpec for compliance
18 |  | Md |  |  | string | 16 |  |  |  | M | S | Model | Manufacturer specific value (32 chars)
34 |  | Opt |  |  | string | 8 |  |  |  |  | S | Options | Manufacturer specific value (16 chars)
42 |  | Vr |  |  | string | 8 |  |  |  |  | S | Version | Manufacturer specific value (16 chars)
50 |  | SN |  |  | string | 16 |  |  |  | M | S | Serial Number | Manufacturer specific value (32 chars)
66 |  | DA |  |  | uint16 |  |  |  | RW |  |  | Device Address | Modbus device address

## 64500
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | system |  |  | group
0 |  | ID | 64500 |  | uint16 |  |  |  | R | M |  | Counter Model | Include this model for energy counter monitoring
1 |  | L | 14 (9 used) |  | uint16 |  |  |  | R | M |  |  | Model Length
2 |  | RunTime |  |  | float32 | 2 |  | s | R |  |  | Time | System Time since powerup in seconds
4 |  | CPU |  |  | uint16 |  |  | % | R
5 |  | Events |  |  | bitfield32 | 2 |  |  | RW | M |  | System Events | Events, generated by code.
|  | Start / Restart | 0 | [8 empty] | Unit Start | Power cycle included
|  | Config Change | 1 | [8 empty] | Configuration Changed | E.g. number of devices changed, new one(s) were added
|  | Device Detection | 2 | [8 empty] | Detection Processing | Devices are being scanned
|  | Modbus WDOG | 3 | [8 empty] | Modbus Watchdog | Remote master device stopped controlling us - purpose is to allow e.g. battery charge stop.
|  | Lua Error / Warning | 4 | [8 empty] | Lua Error or Warning | Lua script error stops its processing. This allows to detect such situation. E.g. email is a good response to this event.
|  | reserved | 5 .. 31 | [8 empty] | Reserved Bits
7 |  | Status |  |  | bitfield32 | 2 |  |  | R | M |  | System Status | Status, generated by code.
|  | reserved | 0 .. 1
|  | Device Detection | 2 | [8 empty] | Device Detection | Bit is set while Device Detection is in progress
|  | Modbus WDOG | 3 | [8 empty] | Modbus Watchdog | Remote master device stopped controlling us - purpose is to allow e.g. battery charge stop.
|  | reserved | 4 .. 31 | [8 empty] | Reserved Bits
9 |  | Command |  |  | enum32 | 2 |  |  | R | M |  | System Commands
|  | reserved | 0 .. 31

## 64501
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | system |  |  | group
0 |  | ID | 64501 |  | uint16 |  |  |  | R | M |  | Digital Input Model | Include this model for Digital Input monitoring
1 |  | L | 1 + (13 * 13) = 170 |  | uint16 |  |  |  | R | M |  |  | Model Length
2 |  | N |  |  | count |  |  |  | R | M |  | Digital Input Count | Number of Digital Input Repeating blocks
|  | inputs.digital |  |  | group
| 0 | ID |  |  | uint16 |  |  |  | R |  |  | Digital Input ID | Digital Input ID
| 1 | Name |  |  | string | 11 |  |  | R | M |  | Digital Input Name | Digital Input Name from SM2 Digital Input Settings
| 12 | DIValue |  |  | enum16 |  |  |  | R | M |  | Digital Input Value | Digital Input Value (high/low)
|  | Input Low | 0 | [8 empty] | Low
|  | Input High | 1 | [8 empty] | High

## 64502
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | system |  |  | group
0 |  | ID | 64502 |  | uint16 |  |  |  | R | M |  | Digital Output Model | Include this model for Digital Output monitoring/control
1 |  | L | 1 + (10 * 13) = 131 |  | uint16 |  |  |  | R | M |  |  | Model Length
2 |  | N |  |  | count |  |  |  | R | M |  | Digital Output Count | Number of Digital Output Repeating blocks
|  | outputs.digital |  |  | group
| 0 | ID |  |  | uint16 |  |  |  | R |  |  | Digital Output ID | Digital Output ID
| 1 | Name |  |  | string | 11 |  |  | R | M |  | Digital Output Name | Digital Output Name from SM2 Digital Output Settings
| 12 | DOState |  |  | enum16 |  |  |  | RW | M |  | Digital Output State | Digital Output state (open/closed)
|  | Output Open | 0 | [8 empty] | open
|  | Output Closed | 1 | [8 empty] | closed

## 64503
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | system |  |  | group
0 |  | ID | 64503 |  | uint16 |  |  |  | R | M |  | Counter Model | Include this model for energy counter monitoring
1 |  | L | 1 + (13 * 20) = 261 |  | uint16 |  |  |  | R | M |  |  | Model Length
2 |  | N |  |  | count |  |  |  | R | M |  | Counter Count | Number of Counter Repeating blocks
|  | counter |  |  | group
| 0 | ID |  |  | uint16 |  |  |  | R |  |  | Counter ID | Counter ID
| 1 | Name |  |  | string | 11 |  |  | R | M |  | Counter Name | Counter Name from SM2 Counter Settings
| 12 | Today |  |  | float32 | 2 |  | Wh / m3 | R |  |  | Today Wh / m3 | Today Energy / Volume (Wh / m3)
| 14 | Total |  |  | float32 | 2 |  | Wh / m3 | R | M |  | Total Wh / m3 | Total Energy / Volume (Wh / m3)
| 16 | P/Q |  |  | float32 | 2 |  | W / l /h | R |  |  | Power / FlowRate | Immediate Power or Flowrate (W / l / h)
| 18 | CtType |  |  | enum16 |  |  |  | R |  |  | Counter Type | Type of the counter
|  | Electrometer Production | 0 | [8 empty] | Production from Electrometer
|  | Electrometer Consumption | 1 | [8 empty] | Consumption from Electrometer
|  | Electrometer Supply DS | 2 | [8 empty] | Supply to DS
|  | Electrometer Consumpt. DS | 3 | [8 empty] | Consumption from DS
|  | Gas Consumption | 4 | [8 empty] | Gas Consumption
|  | Water Consumption | 5 | [8 empty] | Water Consumption
|  | Inverter Production | 6 | [8 empty] | Production from Inverters
|  | Tracker Production | 7 | [8 empty] | Production from Trackers
|  | Battery Charge | 8 | [8 empty] | Energy stored into Battery
|  | Battery Discharge | 9 | [8 empty] | Energy supplied from Battery
|  | Meter Production | 10 | [8 empty] | Production from Meter
|  | Meter Consumption | 11 | [8 empty] | Consumption from Meter
|  | Meter Supply DS | 12 | [8 empty] | Supply to DS
|  | Meter Consumption DS | 13 | [8 empty] | Consumption from DS
|  | LUA Script Energy | 14 | [8 empty] | Energy computed by LUA Script
|  | LUA Script Volume | 15 | [8 empty] | Volume computed by LUA Script
| 19 | CtUnit |  |  | enum16 |  |  |  | R |  |  | Counter Unit | Unit of the Total value (Wh/m3)
|  | Wh | 0 | [8 empty] | Energy
|  | m3 | 1 | [8 empty] | Volume

## 64723
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | controls |  |  | group | [6 empty] | Immediate Controls | Immediate System Controls
0 |  | ID | 64723 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L | 25 (17 used) |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | PLimPct1) |  |  | uint16 |  | PLimPct_SF | % WMax | RW | M |  | WMaxLimPct | Set power output to specified level.
3 |  | PLim_Ena1) |  |  | enum16 |  |  |  | RW | M |  | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control.
|  | DISABLED | 0
|  | ENABLED | 1
4 |  | PFSet1) |  |  | int16 |  | PFSet_SF | cos() | RW | M |  | OutPFSet | Set power factor to specific value - cosine of angle.
5 |  | PFSet_Ena1) |  |  | enum16 |  |  |  | RW | M |  | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control.
|  | DISABLED | 0
|  | ENABLED | 1
6 |  | QPMaxPct |  |  | int16 |  | QPct_SF | % WMax | RW |  |  | VArWMaxPct | Reactive power in percent of WMax.
7 |  | QMaxPct |  |  | int16 |  | QPct_SF | % VArMax | RW |  |  | VArMaxPct | Reactive power in percent of VArMax.
8 |  | QAvalPct |  |  | int16 |  | QPct_SF | % VArAval | RW |  |  | VArAvalPct | Reactive power in percent of VArAval.
9 |  | QPctMod |  |  | enum16 |  |  |  | RW |  |  | VArPct_Mod | Enumerated value. VAR percent limit mode.
|  | NONE | 0
|  | WMax | 1
|  | VArMax | 2
|  | VArAval | 3
10 |  | QPct_Ena |  |  | enum16 |  |  |  | RW | M |  | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control.
0
1
11 |  | PMax_P1) |  |  | enum16 |  | PLimPct_SF | % WMax | RW | M |  | WMax_Pn | Set power output to specified Pn level.
|  | 0 % | 1
|  | 30 % | 2
|  | 50 % | 4
|  | 60 % | 8
|  | 75 % | 16
|  | 100 % | 32
12 |  | QMax_P1) |  |  | enum16 |  | PFSet_SF | cos() | RW | M |  | VAr_QLCn | Set power factor to specific QLCn value - cosine of angle.
|  | -0.95 ¦ Q_QL375 | 1 | [8 empty] | VAr_QL375 | -0.95
|  | -0.97 ¦ Q_QL185 | 2 | [8 empty] | VAr_QL185 | -0.97
|  | 1 ¦ Q_Q0 | 4 | [8 empty] | VAr_Q0 | -1.00
|  | 0.97 ¦ Q_QC185 | 8 | [8 empty] | VAr_QC185 | 0.97
|  | 0.95 ¦ Q_QC375 | 16 | [8 empty] | VAr_QC375 | 0.95
13 |  | QStep | 200 |  | uint16 |  |  |  | RW
14 |  | QUp |  |  | enum16 |  |  |  | RW
|  | NONE | 0
|  | PROCESS | 1
15 |  | QDwn |  |  | enum16 |  |  |  | RW
|  | NONE | 0
|  | PROCESS | 1
16 |  | PLimPct_SF | -2 |  | sunssf 2) |  |  |  | R | M |  | PLimPct_SF | Scale factor for power output percent.
17 |  | PFSet_SF | -3 |  | sunssf 2) |  |  |  | R | M |  | PFSet_SF | Scale factor for power factor.
18 |  | QPct_SF | -2 |  | sunssf 2) |  |  |  | R |  |  | QPct_SF | Scale factor for reactive power percent.
1) Variable is supported in Lua script
2) Scale factor, i.e. 10^scale_factor, e.g. -2 → 10^-2 ~ * 0.01

## 64700
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | power system |  |  | group | [6 empty] | Supply Point | Include this model for energy generator
0 |  | ID | 64700 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L | 1 + (2 *32) = 65 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | N |  |  | count |  |  |  | R | M |  | Number of Sites
|  | point.supply |  |  | group
| 0 | SxID1) 2) |  |  | uint16 |  |  |  | R |  |  | Input ID
| 1 | SxULvl1) |  |  | enum16 |  |  |  | R |  |  | Voltage level (0.4/10/22/35/110 [kV])
|  | 0.4 | 4
|  | 10 | 100
|  | 22 | 220
|  | 35 | 350
|  | 110 | 1100
| 2 | SxUVal1) |  |  | float32 | 2 |  |  | R |  |  | Voltage Value
| 4 | SxIL21) 2) |  |  | float32 | 2 |  | A | R | M |  | Phase 2 Current
| 6 | SxUsAvg1) 2) |  |  | float32 | 2 |  | V | R | M |  | Average Voltage
| 8 | SxP1) 2) |  |  | float32 | 2 |  | W | R | M |  | Active Power
| 10 | SxQ1) 2) |  |  | float32 | 2 |  | VAr | R | M |  | Reactive Power
| 12 | SxCosFi 1) 2) |  |  | float32 | 2 |  | - | R |  |  | Power Factor
| 14 | SxFreq 1) 2) |  |  | float32 | 2 |  | Hz | R |  |  | Frequency
| 16 | SxQMSt1) 2) |  |  | enum16 |  |  |  | R |  |  | Vypínač QM - stav
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 17 | SxQ1St1) 2) |  |  | enum16 |  |  |  | R |  |  | Odpojovač přípojnicový Q6 - stav
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 18 | SxQ6St1) 2) |  |  | enum16 |  |  |  | R |  |  | Odpojovač vývodový Q6 - stav
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 19 | SxQE6St1) 2) |  |  | enum16 |  |  |  | R |  |  | Uzemňovač vývodový QE6 - stav
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 20 | SxQS1St1) 2) |  |  | enum16 |  |  |  | R |  |  | Odpínač QS1
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 21 | SxQSF1St1) 2) |  |  | enum16 |  |  |  | R |  |  | Odpínač s pojistkou QSF1
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 22 | SxFA1St1) 2) |  |  | enum16 |  |  |  | R |  |  | Jistič FA1
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 23 | SxProt1) 2) |  |  | enum16 |  |  |  | R |  |  | Ochrany - působení ochran
|  | OFF | 0
|  | ON | 1
| 24 | SxPFail1) 2) |  |  | enum16 |  |  |  | R |  |  | Ochrany - vnitřní porucha
|  | OFF | 0
|  | ON | 1
| 25 | SxTest1) 2) |  |  | enum16 |  |  |  | R |  |  | Zkušební vypínač
|  | OFF | 0
|  | ON | 1
| 26 | SxUCFail1) 2) |  |  | enum16 |  |  |  | R |  |  | Ztráta ovládacího napětí
|  | OFF | 0
|  | ON | 1
| 27 | SxQMCmd1) 2) |  |  | enum16 |  |  |  | RW |  |  | Vypínač QM – povel
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 28 | SxQS1Cmd1) 2) |  |  | enum16 |  |  |  | RW |  |  | Odpínač QS1 – povel
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 29 | SxQSF1Cmd1) 2) |  |  | enum16 |  |  |  | RW |  |  | Odpínač s pojistkou QSF1 – povel
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 30 | SxFA1Cmd1) 2) |  |  | enum16 |  |  |  | RW |  |  | Jistič FA1 – povel
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 31 | SxTestCmd1) 2) |  |  | enum16 |  |  |  | RW |  |  | Zkušební vypínač – povel
|  | OFF | 0
|  | ON | 1
1) Variable is supported in Lua script
2) x = i, where i is a point index (in range 1 - N). E.g. for index 2 the variable name is in form S1UsAvg.
3) Malfunction. E.g. any signal is not present.
4) All signals are present, but not all are same or intermediate position.
TODO: SxFU1St pro ČEZ

## 64701
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | power system |  |  | group | [6 empty] | Breakdown Point | Include this model for energy generator
0 |  | ID | 64701 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L | 1 + (3 * 18) = 55 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | N |  |  | count |  |  |  | R |  |  | Number of Sites
|  | point.breakdown |  |  | group
| 0 | BxID1) 2) |  |  | uint16 |  |  |  | R |  |  | Input ID
| 1 | BxIL21) 2) |  |  | float32 | 2 |  | A | R | M |  | Phase 2 Current
| 3 | BxUsAvg1) 2) |  |  | float32 | 2 |  | V | R | M |  | Average Voltage
| 5 | BxP1) 2) |  |  | float32 | 2 |  | W | R | M |  | Active Power
| 7 | BxQ1) 2) |  |  | float32 | 2 |  | VAr | R | M |  | Reactive Power
| 9 | BxCosFi 1) 2) |  |  | float32 | 2 |  | - | R |  |  | Power Factor
| 11 | BxFreq 1) 2) |  |  | float32 | 2 |  | Hz | R |  |  | Frequency
| 13 | BxQMSt1) 2) |  |  | enum16 |  |  |  | R |  |  | Contactor State
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 14 | BxFA1St1) 2) |  |  | enum16 |  |  |  | R |  |  | Circuit Braker State
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 15 | BxProt1) 2) |  |  | enum16 |  |  |  | R |  |  | U-f Guard Protection
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 16 | BxPFail1) 2) |  |  | enum16 |  |  |  | R |  |  | Protection – Internal failure
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
| 17 | BxQMCmd1) 2) |  |  | enum16 |  |  |  | RW |  |  | Circuit Braker - Command
|  | INDETERMINATE0 3) | 0
|  | All OFF | 1
|  | All ON | 2
|  | INDETERMINATE3 4) | 3
1) Variable is supported in Lua script
2) x = i, where i is a point index (in range 1 - N). E.g. for index 2 the variable name is in form B2UsAvg.
3) Malfunction. E.g. any signal is not present.
4) All signals are present, but not all are same or intermediate position.

## 64790
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | measurement |  |  | group | [6 empty] | Local Measurement | Sensors and battery measurements.
0 |  | ID | 64790 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L | 10 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Pinst |  |  | float32 | 2 |  | Wp | R |  |  | Nominal Power Output
4 |  | TOut1) |  |  | float32 | 2 |  | °C | R |  |  | Outside Temperature
6 |  | Sol1) |  |  | float32 | 2 |  | W/m2 | R |  |  | Irradiation
8 |  | WS1) |  |  | float32 | 2 |  | m/s | R |  |  | Wind Speed
10 |  | BSoC1) |  |  | float32 | 2 |  | % | R |  |  | Battery Capacity | State of Charge
12 |  | BSoH1) |  |  | float32 | 2 |  | % | R |  |  | Battery Health | State of Health
1) Variable is supported in Lua script