## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.4 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number
Date | 2018-01-17 11:50:44
Manufacturer Name
Product Name
Product Models
Product Description

## Testing Info
Submitter
Email
Phone
Interface Type | TCP
IP Address | 192.168.1.177
IP Port | 502
Slave Id | 1

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 65
40004 | Manufacturer (Mn) |  |  | Studer | R
40020 | Model (Md) |  |  | XTM 2000-12V (L2) | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | unimplemented | R
40052 | Serial Number (SN) |  |  | 3D034E01 | R
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 111
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40069 | ID |  |  | 111
40070 | L |  |  | 60
40071 | Amps (A) |  |  | unimplemented | R
40073 | Amps PhaseA (AphA) |  |  | supported | R
40075 | Amps PhaseB (AphB) |  |  | unimplemented | R
40077 | Amps PhaseC (AphC) |  |  | unimplemented | R
40079 | Phase Voltage AB (PPVphAB) |  |  | unimplemented | R
40081 | Phase Voltage BC (PPVphBC) |  |  | unimplemented | R
40083 | Phase Voltage CA (PPVphCA) |  |  | unimplemented | R
40085 | Phase Voltage AN (PhVphA) |  |  | supported | R
40087 | Phase Voltage BN (PhVphB) |  |  | unimplemented | R
40089 | Phase Voltage CN (PhVphC) |  |  | unimplemented | R
40091 | Watts (W) |  |  | supported | R
40093 | Hz |  |  | supported | R
40095 | VA |  |  | supported | R
40097 | VAr |  |  | unimplemented | R
40099 | PF |  |  | unimplemented | R
40101 | WattHours (WH) |  |  | supported | R
40103 | DC Amps (DCA) |  |  | supported | R
40105 | DC Voltage (DCV) |  |  | supported | R
40107 | DC Watts (DCW) |  |  | unimplemented | R
40109 | Cabinet Temperature (TmpCab) |  |  | supported | R
40111 | Heat Sink Temperature (TmpSnk) |  |  | unimplemented | R
40113 | Transformer Temperature (TmpTrns) |  |  | unimplemented | R
40115 | Other Temperature (TmpOt) |  |  | unimplemented | R
40117 | Operating State (St) |  |  | supported | R
|  |  | ggOFF | supported
|  |  | ggSLEEPING | supported
|  |  | ggSTARTING | supported
|  |  | MPPT (ggMPPT) | supported
|  |  | ggTHROTTLED | supported
|  |  | ggSHUTTING_DOWN | supported
|  |  | ggFAULT | supported
|  |  | ggSTANDBY | supported
|  |  | Off (None) | supported
|  |  | Sleeping (None) | supported
|  |  | Starting (None) | supported
|  |  | Throttled (None) | supported
|  |  | Shutting down (None) | supported
|  |  | Fault (None) | supported
|  |  | Standby (None) | supported
40118 | Vendor Operating State (StVnd) |  |  | unimplemented | R
40119 | Event1 (Evt1) |  |  | unimplemented | R
|  |  | Ground fault (GROUND_FAULT) | supported
|  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  | AC disconnect open (AC_DISCONNECT) | supported
|  |  | DC disconnect open (DC_DISCONNECT) | supported
|  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  | Cabinet open (CABINET_OPEN) | supported
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over temperature (OVER_TEMP) | supported
|  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  | Under temperature (UNDER_TEMP) | supported
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported
40121 | Event Bitfield 2 (Evt2) |  |  | unimplemented | R
40123 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | unimplemented | R
40125 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | unimplemented | R
40127 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | unimplemented | R
40129 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | unimplemented | R

## 160
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40131 | ID |  |  | 160
40132 | L |  |  | 28
40133 | Current Scale Factor (DCA_SF) |  |  | -2 | R
40134 | Voltage Scale Factor (DCV_SF) |  |  | -2 | R
40135 | Power Scale Factor (DCW_SF) |  |  | unimplemented | R
40136 | Energy Scale Factor (DCWH_SF) |  |  | -2 | R
40137 | Global Events (Evt) |  |  | unimplemented | R
|  |  | Ground Fault (GROUND_FAULT) | supported
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | supported
|  |  | Reserved (RESERVED) | supported
|  |  | DC Disconnect (DC_DISCONNECT) | supported
|  |  | Cabinet Open (CABINET_OPEN) | supported
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over Temperature (OVER_TEMP) | supported
|  |  | Blown Fuse (BLOWN_FUSE) | supported
|  |  | Under Temperature (UNDER_TEMP) | supported
|  |  | Memory Loss (MEMORY_LOSS) | supported
|  |  | Arc Detection (ARC_DETECTION) | supported
|  |  | Test Failed (TEST_FAILED) | supported
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | supported
|  |  | Over Current (INPUT_OVER_CURRENT) | supported
40139 | Number of Modules (N) |  |  | supported | R
40140 | Timestamp Period (TmsPer) |  |  | unimplemented | R
40141 | Input ID (ID) | 1 |  | unimplemented | R
40142 | Input ID Sting (IDStr) | 1 |  | unimplemented | R
40150 | DC Current (DCA) | 1 |  | supported | R
40151 | DC Voltage (DCV) | 1 |  | supported | R
40152 | DC Power (DCW) | 1 |  | unimplemented | R
40153 | Lifetime Energy (DCWH) | 1 |  | unimplemented | R
40155 | Timestamp (Tms) | 1 |  | unimplemented | R
40157 | Temperature (Tmp) | 1 |  | unimplemented | R
40158 | Operating State (DCSt) | 1 |  | unimplemented | R
|  |  | Off (OFF) | supported
|  |  | Sleeping (SLEEPING) | supported
|  |  | Starting (STARTING) | supported
|  |  | MPPT | supported
|  |  | Throttled (THROTTLED) | supported
|  |  | Shutting Down (SHUTTING_DOWN) | supported
|  |  | Fault (FAULT) | supported
|  |  | Standby (STANDBY) | supported
|  |  | Test (TEST) | supported
|  |  | Reserved (RESERVED) | supported
40159 | Module Events (DCEvt) | 1 |  | unimplemented | R
|  |  | Ground Fault (GROUND_FAULT) | supported
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | supported
|  |  | Reserved (RESERVED) | supported
|  |  | DC Disconnect (DC_DISCONNECT) | supported
|  |  | Cabinet Open (CABINET_OPEN) | supported
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over Temperature (OVER_TEMP) | supported
|  |  | Blown Fuse (BLOWN_FUSE) | supported
|  |  | Under Temperature (UNDER_TEMP) | supported
|  |  | Memory Loss (MEMORY_LOSS) | supported
|  |  | Arc Detection (ARC_DETECTION) | supported
|  |  | Test Failed (TEST_FAILED) | supported
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | supported
|  |  | Over Current (INPUT_OVER_CURRENT) | supported

## 64400
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40161 | ID |  |  | 64400
40162 | L |  |  | 5
40163 | Parameter Number (ParNum) |  |  | supported | RW
40164 | Parameter Type (ParType) |  |  | supported | RW
|  |  | Integer32 (Integer) | supported
|  |  | Enum16 (Enum) | supported
|  |  | Integer32 (Byte) | supported
|  |  | Float32 (Float) | supported
40165 | Parameter Value (ParValue) |  |  | supported | RW
40167 | Parameter Command (ParCmd) |  |  | supported | RW
|  |  | Write Command (WRITE) | supported
|  |  | Read Command (READ) | supported

## 64410
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40168 | ID |  |  | 64410
40169 | L |  |  | 98
40170 | XT Model (xtModel) |  |  | unimplemented | R
40186 | XT FID (xtFID) |  |  | unimplemented | R
40202 | Software Version (xtSwVersion) |  |  | unimplemented | R
40218 | ID Battery Voltage (xtIdBatteryVoltage) |  |  | supported | R
40220 | Defined Phase (xtDefinedPhase) |  |  | supported | R
40222 | State (xtState) |  |  | supported | R
|  |  | Offline (off) | supported
|  |  | Online (on) | supported
40223 | Battery Voltage (xtBatteryVoltage) |  |  | supported | R
40225 | Battery Charge Current (xtBatteryChargeCurrent) |  |  | supported | R
40227 | Battery Cycle Current (xtBatteryCyclePhase) |  |  | supported | R
|  |  | Invalid Value (invalidValue) | supported
|  |  | Bulk (bulk) | supported
|  |  | Absorption (absorption) | supported
|  |  | Equalise (equalise) | supported
|  |  | Floating (floating) | supported
|  |  | R Floating (rFloating) | supported
|  |  | Per Absorption (perAbsorption) | supported
|  |  | Mixing (mixing) | supported
|  |  | Forming (forming) | supported
40228 | Input Voltage (xtInVoltage) |  |  | supported | R
40230 | Input Voltage Min (xtInVoltageMin) |  |  | supported | R
40232 | Input Voltage Max (xtInVoltageMax) |  |  | supported | R
40234 | Input Current (xtInCurrent) |  |  | supported | R
40236 | Input Current Min (xtInCurrentMin) |  |  | supported | R
40238 | Input Current Max (xtInCurrentMax) |  |  | supported | R
40240 | Input Frequency (xtInFrequency) |  |  | supported | R
40242 | Input Frequency Min (xtInFrequencyMin) |  |  | supported | R
40244 | Input Frequency Max (xtInFrequencyMax) |  |  | supported | R
40246 | Input Apparent Power (xtInApparentPower) |  |  | supported | R
40248 | Input Active Power (xtInActivePower) |  |  | supported | R
40250 | Output Voltage (xtOutVoltage) |  |  | supported | R
40252 | Output Current (xtOutCurrent) |  |  | supported | R
40254 | Output Frequency (xtOutFrequency) |  |  | supported | R
40256 | Output Apparent Power (xtOutApparentPower) |  |  | supported | R
40258 | Output Active Power (xtOutActivePower) |  |  | supported | R
40260 | Operating State (xtOperatingState) |  |  | unimplemented | R
|  |  | Invalid Value (invalidValue) | supported
|  |  | Inverter (inverter) | supported
|  |  | Charger (charger) | supported
|  |  | Boost (boost) | supported
|  |  | Injection (injection) | supported
40261 | State of Transfer Relay (xtTransferRelay) |  |  | supported | R
|  |  | Opened (opened) | supported
|  |  | Closed (closed) | supported
40262 | Remote Entry State (xtRemoteEntryState) |  |  | supported | R
|  |  | Remote Entry 0 (rmEn0) | supported
|  |  | Remote Entry 1 (rmEn1) | supported
40263 | Battery Priority Active (xtBatteryPriorityActive) |  |  | supported | R
40264 | State of Auxillary Relay 1 (xtAUX1RelayState) |  |  | supported | R
|  |  | Opened (opened) | supported
|  |  | Closed (closed) | supported
40265 | Relay AUX 1 Mode (xtAUX1RelayMode) |  |  | supported | R
|  |  | Invalid Value (invalidValue) | supported
|  |  | Automatic (automatic) | supported
|  |  | Reversed Automatic (reversedAutomatic) | supported
|  |  | Manual On (manualOn) | supported
|  |  | Manual Off (manualOff) | supported
|  |  | Generator Start (coupledForGeneratorStart) | supported
40266 | State of Auxillary Relay 2 (xtAUX2RelayState) |  |  | supported | R
|  |  | Opened (opened) | supported
|  |  | Closed (closed) | supported
40267 | Relay AUX 2 Mode (xtAUX2RelayMode) |  |  | supported | R
|  |  | Invalid Value (invalidValue) | supported
|  |  | Automatic (automatic) | supported
|  |  | Reversed Automatic (reversedAutomatic) | supported
|  |  | Manual On (manualOn) | supported
|  |  | Manual Off (manualOff) | supported
|  |  | Generator Start (coupledForGeneratorStart) | supported