## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.4 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number
Date | 2018-01-17 12:02:17
Manufacturer Name
Product Name
Product Models
Product Description

## Testing Info
Submitter
Email
Phone
Interface Type | TCP
IP Address | 192.168.1.177
IP Port | 502
Slave Id | 4

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 65
40004 | Manufacturer (Mn) |  |  | Studer | R
40020 | Model (Md) |  |  | BSP 500-12V | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | unimplemented | R
40052 | Serial Number (SN) |  |  | 3D149C50 | R
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 124
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40069 | ID |  |  | 124
40070 | L |  |  | 24
40071 | WChaMax |  |  | unimplemented | RW
40072 | WChaGra |  |  | unimplemented | RW
40073 | WDisChaGra |  |  | unimplemented | RW
40074 | StorCtl_Mod |  |  | unimplemented | RW
|  |  | CHARGE | supported
|  |  | DiSCHARGE | supported
40075 | VAChaMax |  |  | unimplemented | RW
40076 | MinRsvPct |  |  | unimplemented | RW
40077 | ChaState |  |  | supported | R
40078 | StorAval |  |  | unimplemented | R
40079 | InBatV |  |  | supported | R
40080 | ChaSt |  |  | unimplemented | R
|  |  | OFF | supported
|  |  | EMPTY | supported
|  |  | DISCHARGING | supported
|  |  | CHARGING | supported
|  |  | FULL | supported
|  |  | HOLDING | supported
|  |  | TESTING | supported
40081 | OutWRte |  |  | unimplemented | RW
40082 | InWRte |  |  | unimplemented | RW
40083 | InOutWRte_WinTms |  |  | unimplemented | RW
40084 | InOutWRte_RvrtTms |  |  | unimplemented | RW
40085 | InOutWRte_RmpTms |  |  | unimplemented | RW
40086 | ChaGriSet |  |  | unimplemented | RW
|  |  | PV | supported
|  |  | GRID | supported
40087 | WChaMax_SF |  |  | unimplemented | R
40088 | WChaDisChaGra_SF |  |  | unimplemented | R
40089 | VAChaMax_SF |  |  | unimplemented | R
40090 | MinRsvPct_SF |  |  | unimplemented | R
40091 | ChaState_SF |  |  | -2 | R
40092 | StorAval_SF |  |  | unimplemented | R
40093 | InBatV_SF |  |  | -2 | R
40094 | InOutWRte_SF |  |  | unimplemented | R

## 64400
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40095 | ID |  |  | 64400
40096 | L |  |  | 5
40097 | Parameter Number (ParNum) |  |  | supported | RW
40098 | Parameter Type (ParType) |  |  | supported | RW
|  |  | Integer32 (Integer) | supported
|  |  | Enum16 (Enum) | supported
|  |  | Integer32 (Byte) | supported
|  |  | Float32 (Float) | supported
40099 | Parameter Value (ParValue) |  |  | supported | RW
40101 | Parameter Command (ParCmd) |  |  | supported | RW
|  |  | Write Command (WRITE) | supported
|  |  | Read Command (READ) | supported

## 64413
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40102 | ID |  |  | 64413
40103 | L |  |  | 64
40104 | BSP Model (bspModel) |  |  | unimplemented | R
40120 | BSP FID (bspFID) |  |  | unimplemented | R
40136 | Software Version (bspSwVersion) |  |  | unimplemented | R
40152 | Battery Voltage (bspBatteryVoltage) |  |  | supported | R
40154 | Battery Current (bspBatteryCurrent) |  |  | supported | R
40156 | State Of Charge (bspStateOfCharge) |  |  | supported | R
40158 | BSP Power (bspPower) |  |  | supported | R
40160 | Battery Temperature (bspBatteryTemp) |  |  | supported | R
40162 | Remaining Autonomy (bspRemainingAutonomy) |  |  | supported | R
40164 | Charged Today (bspAhChargedToday) |  |  | supported | R
40166 | Discharge Today (bspAhDischargedToday) |  |  | supported | R