## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.4 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number
Date | 2018-01-17 11:55:04
Manufacturer Name
Product Name
Product Models
Product Description

## Testing Info
Submitter
Email
Phone
Interface Type | TCP
IP Address | 192.168.1.177
IP Port | 502
Slave Id | 2

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 65
40004 | Manufacturer (Mn) |  |  | Studer | R
40020 | Model (Md) |  |  | VT 65-12.0V | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | unimplemented | R
40052 | Serial Number (SN) |  |  | 3D1E0001 | R
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 160
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40069 | ID |  |  | 160
40070 | L |  |  | 48
40071 | Current Scale Factor (DCA_SF) |  |  | -2 | R
40072 | Voltage Scale Factor (DCV_SF) |  |  | -2 | R
40073 | Power Scale Factor (DCW_SF) |  |  | -2 | R
40074 | Energy Scale Factor (DCWH_SF) |  |  | -2 | R
40075 | Global Events (Evt) |  |  | unimplemented | R
|  |  | Ground Fault (GROUND_FAULT) | supported
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | supported
|  |  | Reserved (RESERVED) | supported
|  |  | DC Disconnect (DC_DISCONNECT) | supported
|  |  | Cabinet Open (CABINET_OPEN) | supported
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over Temperature (OVER_TEMP) | supported
|  |  | Blown Fuse (BLOWN_FUSE) | supported
|  |  | Under Temperature (UNDER_TEMP) | supported
|  |  | Memory Loss (MEMORY_LOSS) | supported
|  |  | Arc Detection (ARC_DETECTION) | supported
|  |  | Test Failed (TEST_FAILED) | supported
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | supported
|  |  | Over Current (INPUT_OVER_CURRENT) | supported
40077 | Number of Modules (N) |  |  | supported | R
40078 | Timestamp Period (TmsPer) |  |  | unimplemented | R
40079 | Input ID (ID) | 1 |  | unimplemented | R
40080 | Input ID Sting (IDStr) | 1 |  | unimplemented | R
40088 | DC Current (DCA) | 1 |  | supported | R
40089 | DC Voltage (DCV) | 1 |  | supported | R
40090 | DC Power (DCW) | 1 |  | supported | R
40091 | Lifetime Energy (DCWH) | 1 |  | supported | R
40093 | Timestamp (Tms) | 1 |  | unimplemented | R
40095 | Temperature (Tmp) | 1 |  | unimplemented | R
40096 | Operating State (DCSt) | 1 |  | unimplemented | R
|  |  | Off (OFF) | supported
|  |  | Sleeping (SLEEPING) | supported
|  |  | Starting (STARTING) | supported
|  |  | MPPT | supported
|  |  | Throttled (THROTTLED) | supported
|  |  | Shutting Down (SHUTTING_DOWN) | supported
|  |  | Fault (FAULT) | supported
|  |  | Standby (STANDBY) | supported
|  |  | Test (TEST) | supported
|  |  | Reserved (RESERVED) | supported
40097 | Module Events (DCEvt) | 1 |  | unimplemented | R
|  |  | Ground Fault (GROUND_FAULT) | supported
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | supported
|  |  | Reserved (RESERVED) | supported
|  |  | DC Disconnect (DC_DISCONNECT) | supported
|  |  | Cabinet Open (CABINET_OPEN) | supported
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over Temperature (OVER_TEMP) | supported
|  |  | Blown Fuse (BLOWN_FUSE) | supported
|  |  | Under Temperature (UNDER_TEMP) | supported
|  |  | Memory Loss (MEMORY_LOSS) | supported
|  |  | Arc Detection (ARC_DETECTION) | supported
|  |  | Test Failed (TEST_FAILED) | supported
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | supported
|  |  | Over Current (INPUT_OVER_CURRENT) | supported
40099 | Input ID (ID) | 2 |  | unimplemented | R
40100 | Input ID Sting (IDStr) | 2 |  | unimplemented | R
40108 | DC Current (DCA) | 2 |  | unimplemented | R
40109 | DC Voltage (DCV) | 2 |  | supported | R
40110 | DC Power (DCW) | 2 |  | supported | R
40111 | Lifetime Energy (DCWH) | 2 |  | unimplemented | R
40113 | Timestamp (Tms) | 2 |  | unimplemented | R
40115 | Temperature (Tmp) | 2 |  | unimplemented | R
40116 | Operating State (DCSt) | 2 |  | unimplemented | R
40117 | Module Events (DCEvt) | 2 |  | unimplemented | R

## 64400
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40119 | ID |  |  | 64400
40120 | L |  |  | 5
40121 | Parameter Number (ParNum) |  |  | supported | RW
40122 | Parameter Type (ParType) |  |  | supported | RW
|  |  | Integer32 (Integer) | supported
|  |  | Enum16 (Enum) | supported
|  |  | Integer32 (Byte) | supported
|  |  | Float32 (Float) | supported
40123 | Parameter Value (ParValue) |  |  | supported | RW
40125 | Parameter Command (ParCmd) |  |  | supported | RW
|  |  | Write Command (WRITE) | supported
|  |  | Read Command (READ) | supported

## 64411
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40126 | ID |  |  | 64411
40127 | L |  |  | 73
40128 | VT Model (vtModel) |  |  | unimplemented | R
40144 | VT FID (vtFID) |  |  | unimplemented | R
40160 | Software Version (vtSwVersion) |  |  | unimplemented | R
40176 | Battery Nominal Voltage (vtBatteryNominalVoltage) |  |  | supported | R
40178 | State (vtState) |  |  | supported | R
|  |  | Offline (off) | supported
|  |  | Online (on) | supported
40179 | Error Type (vtErrType) |  |  | unimplemented | R
|  |  | No Error (noError) | supported
|  |  | Battery Over Voltage (batteryOverVoltage) | supported
|  |  | Earth (earth) | supported
|  |  | No Battery (noBattery) | supported
|  |  | Over Temperature (overTemperature) | supported
|  |  | PV Over Voltage (pvOverVoltage) | supported
|  |  | Others (others) | supported
|  |  | Driv 12 Voltage (driv12Voltage) | supported
|  |  | Under Current (underCurrent) | supported
|  |  | Int 12 Voltage (int12Voltage) | supported
|  |  | Over Current (overCurrent) | supported
|  |  | Hard Error (hardError) | supported
40180 | Battery Voltage (vtBatteryVoltage) |  |  | supported | R
40182 | Battery Current (vtBatteryCurrent) |  |  | supported | R
40184 | Battery Cycle Phase (vtBatteryCyclePhase) |  |  | supported | R
|  |  | Bulk (bulk) | supported
|  |  | Absorption (absorption) | supported
|  |  | Equalize (equalize) | supported
|  |  | Floating (floating) | supported
|  |  | XTender Slave (xtSlave) | supported
|  |  | VarioTrack Slave (vtSlave) | supported
|  |  | R Floating (rFloating) | supported
|  |  | Per Absorption (perAbsorption) | supported
40185 | Synchronization State (vtSynState) |  |  | supported | R
|  |  | XTender Slave (xtSlave) | supported
|  |  | VarioTrack Slave (vtSlave) | supported
|  |  | VarioTrack Master (vtMaster) | supported
|  |  | Autonomy (autonomy) | supported
|  |  | VarioString Slave (vsSlave) | supported
|  |  | VarioString Master (vsMaster) | supported
40186 | Voltage of the PV generator (vtPVGenVol) |  |  | unimplemented | R
40188 | Power of the PV generator (vtPVGenPow) |  |  | supported | R
40190 | Battery Temperature (vtBatteryTemp) |  |  | supported | R
40192 | Operating Mode (vtOperatingMode) |  |  | supported | R
|  |  | Night (night) | supported
|  |  | Start Up (startUp) | supported
|  |  | Scanning (scanning) | supported
|  |  | Charger (charger) | supported
|  |  | Manual (manual) | supported
|  |  | Security (security) | supported
|  |  | Offline (off) | supported
|  |  | Slave (slave) | supported
|  |  | Charge (charge) | supported
|  |  | Charge Voltage (chargeVoltage) | supported
|  |  | Charge Current (chargeCurrent) | supported
|  |  | Charge Temperature (chargeTemperature) | supported
40193 | State of Auxillary Relay 1 (vtAUX1RelayState) |  |  | supported | R
|  |  | Opened (opened) | supported
|  |  | Closed (closed) | supported
40194 | Relay AUX 1 Mode (vtAUX1RelayMode) |  |  | supported | R
|  |  | Invalid Value (invalidValue) | supported
|  |  | Automatic (automatic) | supported
|  |  | Reversed Automatic (reversedAutomatic) | supported
|  |  | Manual (manualOn) | supported
|  |  | Manual Off (manualOff) | supported
|  |  | Generator Start (coupledForGeneratorStart) | supported
40195 | State of Auxillary Relay 2 (vtAUX2RelayState) |  |  | supported | R
|  |  | Opened (opened) | supported
|  |  | Closed (closed) | supported
40196 | Relay AUX 2 Mode (vtAUX2RelayMode) |  |  | supported | R
|  |  | Invalid Value (invalidValue) | supported
|  |  | Automatic (automatic) | supported
|  |  | Reversed Automatic (reversedAutomatic) | supported
|  |  | Manual (manualOn) | supported
|  |  | Manual Off (manualOff) | supported
|  |  | Generator Start (coupledForGeneratorStart) | supported
40197 | State of Auxillary Relay 3 (vtAUX3RelayState) |  |  | supported | R
|  |  | Opened (opened) | supported
|  |  | Closed (closed) | supported
40198 | Relay AUX 3 Mode (vtAUX3RelayMode) |  |  | supported | R
|  |  | Invalid Value (invalidValue) | supported
|  |  | Automatic (automatic) | supported
|  |  | Reversed Automatic (reversedAutomatic) | supported
|  |  | Manual (manualOn) | supported
|  |  | Manual Off (manualOff) | supported
|  |  | Generator Start (coupledForGeneratorStart) | supported
40199 | State of Auxillary Relay 4 (vtAUX4RelayState) |  |  | supported | R
|  |  | Opened (opened) | supported
|  |  | Closed (closed) | supported
40200 | Relay AUX 4 Mode (vtAUX4RelayMode) |  |  | supported | R
|  |  | Invalid Value (invalidValue) | supported
|  |  | Automatic (automatic) | supported
|  |  | Reversed Automatic (reversedAutomatic) | supported
|  |  | Manual (manualOn) | supported
|  |  | Manual Off (manualOff) | supported
|  |  | Generator Start (coupledForGeneratorStart) | supported